## User Documentation
CSW Savings Calculator
2025-01-13 | date of last revision
version | 2.0.0
author | Solarc Energy Group
General: | This savings calculator generates separate savings for heating, HVAC auxiliaries and cooling based on a data set developed from parametric Energy Plus runs using prototype models
developed for and by BPA. Models address mid-sized offices, large offices, small hotels, large hotels, primary schools, secondary schools, small hospitals., mid-rise multifamily, and low-rise multifamily.
Several user inputs act as pointers to the proper subset of data. Adjustments to the data sub-set are made via regression equations to
account for differences in geography, climate, and HVAC operating hours (for offices), and average occupancy rate (for hotels). The dataset is representative of climate variations throughout United States climate zones.
Limitations: | This calculator is intended for use in building applications with existing single pane windows in the following building and representative electric and gas system types:
1) Mid-sized offices: Packaged VAV with electric reheat terminal units
2) Mid-sized offices: Packaged VAV with hydronic reheat from gas-fired boilers
3) Large offices: Built-up single duct VAV with hydronic reheat from electric resistance boilers.
4) Large offices: Built-up single duct VAV with hydronic reheat from gas-fired boilers.
5) Small hotels: Packaged terminal air conditioning (PTAC) units with electric heat
6) Small hotels: Packaged terminal heat pumps (PTHPs)
7) Large hotels: Distributed 4-pipe fan coil units with electric chiller and electric boiler
8) Large hotels: Distributed 4-pipe fan coil units with electric chiller and gas-fired boiler
9) Primary Schools: Single duct VAV with gas-fired hydronic reheat
10) Primary Schools: Single duct VAV with electric reheat
11) Primary Schools: Distributed 4-pipe fan coil units with electric chiller and electric boiler
12) Primary Schools: Distributed 4-pipe fan coil units with electric chiller and gas-fired boiler.
13) Secondary Schools: Single duct VAV with gas-fired hydronic reheat
14) Secondary Schools: Single duct VAV with electric reheat
15) Secondary Schools: Distributed 4-pipe fan coil units with electric chiller and electric boiler
16) Secondary Schools: Distributed 4-pipe fan coil units with electric chiller and gas-fired boiler.
17) Small Hospital: Single duct VAV with hydronic reheat from electric resistance boiler.
18) Small Hospital: Single duct VAV with hydronic reheat from gas-fired boiler.
19) Mid-rise Multifamily: Single zone fan coil units with electric hot water boiler and air-cooled chiller
20) Mid-rise Multifamily: Single zone fan coil units with gas-fired hot water boiler and air-cooled chiller
21) Low-rise Multifamily: Packaged terminal air conditioning units with electric heat
Instruction for use: | 1. All user input and savings output iresides in one of five building type tabs: Office, Hotel, School, Hospital, or Multifamily.
2. All user input cells contain a comment that provides guidance for the user. Depending on the building type there are (13) or (14) input cells.
3. All savings output cells are calculated and highlighted in yellow.
4. The user selects the closest geograhical location from a lists designating "State" and then "Cities", that then populates the degree-day cells.
Version Note: | This Beta version is populated with savings curves derived with Eplus model data for the building and system types listed above.
Input Cell Descriptions: | 1. Information About Your Project: Input project name, address, and contact information in locations as noted.
2. Project Location (State): This is a pull-down menu inpt. User must select one of 50 states and the District of Columbia.
3. Project Location (City): This is a pull-down menu input. User must select from the list of cities that are generated by the State selection. The list of cities corresponds to the cities for which typical meteorological climate data exist. User should select the city from the list that represents the nearest city to the project location. Selection of city populates the heating and cooling degree-day entries for the project.
4. Electric Utility: This is a text entry, and is not used in the savings calculation. User should enter the name of the servicing electric utility. This information is intended to support the development of an accurate estimate of electric rate.
5. Natural Gas Utility: This is a text entry, and is not used in the savings calculation. User should enter the name of the servicing natural gas utility. If there is no natural gas utility, then enter “N/A.” This information is intended to support the development of an accurate estimate of natural gas rate.
6. Electric Rate, $/kWh:This is a numerical entry and is used to determine electric cost savings, in dollars. The user should enter the cost of electrical energy in $ per kWh. Ideally, this should not include demand charges, utility surcharges, or other charges such as meter charges. It can include taxes or local charges that are assessed on the basis of monthly energy (kWh) use. In simple terms, this entry is intended to be derived by dividing a typical total monthly billing charge for energy only, in $, by the monthly electric energy use in that bill, in kWh. Note that electric rate schedules and billings can be complicated. Commercial accounts can include charges for peak monthly demand (kW), capacity charges, power factor penalties, meter charges, and other categories of charges. In addition, some rate schedules incorporate different rates depending upon time-of-use or magnitude of use (tiered rates). Most time-of use rates charge more for energy used during the utility peak times. Most tiered rates charge less for the highest tier of use. To make the most accurate estimate of energy cost savings, it is important to account for the cost of the electrical energy that will be most affected by the installation of CSW units. This cost is often referred to as the marginal electric rates. A simple way to estimate the marginal rate would be to divide the difference in two monthly billing charges by the difference in those two months energy use. For example, (Jan $ - Dec $) / (Jan kWh – Dec kWh).
7. Natural Gas Rate, $/therm: This is a numerical entry and is used to determine natural gas cost savings, in dollars. The user should enter the average annual cost of natural gas in $ per therm. This should not include utility surcharges, or other charges such as meter charges. In simple terms, this entry is intended to be derived by dividing a typical total monthly billing charge, in $, by the monthly natural gas energy use in that bill, in therms. If gas energy units are not therms, user should convert gas rate to the equivalent cost per therm. For example, gas rate at $6.00 per MMBtu (or deca-therm) would translate to an equivalent rate of $0.60 per therm. Similar to electric rates, some natural gas rate schedules incorporate different rates depending upon time-of-use or magnitude of use (tiered rates). Most time-of use rates charge more for energy used during the winter heating season. Most tiered rates charge slightly less for the highest tier of use. To make the most accurate estimate of energy cost savings, it is important to account for the cost of the natural gas energy that will be most affected by the installation of CSW units. This cost is often referred to as the marginal rate. A simple way to estimate the most applicable marginal rate would be to divide the difference in two wintertime monthly billing charges by the difference in those two months energy use. For example, (Jan $ - Dec $) / (Jan therms – Dec therms).
8. Building Area, Sq.Ft.:This is a numerical entry and is used to determine overall energy savings percentage, reported as Energy Use Intensities (in kBtu/sq.ft.-year.) It is also used to estimate overall peak cooling load reduction at an overall building level, in tons of refrigeration. It is also used in combination with the Number of floors input value, to estimate the window to wall ratio and alert the user when the CSW sq.ft. input may require verification. Building area should represent the conditioned area of all floors above grade. It is recommended to exclude basement area.
9. N o. of floors:This is a numerical whole number entry representing the total number of floors that are included in the Building Area entry. It is used in the logic to to estimate the window to wall ratio and alert the user when the CSW sq.ft. input may require verification. This entry does not directly affect energy savings. For Multifamily buildings, it is used to determine whether the project is Mid-rise (greater than 3 floors) or Low-rise (3 floors or less).
10. HVAC System Type: This is a pull-down menu input variable. The list of choices in the pull-down menu varies with the building type. User must select one of the entries from the pull-down menu (listed and briefly described below). The system type selection is used in the logic to determine the appropriate set of regression curves to reference for savings estimates.
a. Packaged VAV with electric reheat: This represents packaged rooftop variable air volume systems with electric resistance reheat coils in terminal units within ductwork. This is a typical HVAC system type for mid-rise office buildings. This system type can be selected for offices only of any size.
b. Packaged VAV with hydronic reheat: This represented packaged rooftop variable air volume systems with hydronic (hot water) reheat coils in terminal units within ductwork. This is a variation of typical HVAC systems for mid-rise office buildings where a gas-fired hot water boiler is installed in the building to meet system reheat needs. This system type can be selected for offices only of any size.
c. Built-up VAV with hydronic reheat from gas-fired boilers: This represents built-up variable air volume systems where air handling units and reheat coils are served by central chillers and boilers. Reheat coils in terminal units are hydronic (hot water). This is a typical HVAC system for large office buildings. This system type can be selected for offices only of any size.
d. Built-up VAV with hydronic reheat from electric resistance boilers: This represents built-up variable air volume systems where air handling units and reheat coils are served by electric-drive chillers and gas-fired boilers. Reheat coils in terminal units are hydronic (hot water). This is a typical HVAC system for large office buildings. This system type can be selected for offices of any size.
e. Packaged Terminal Air Conditioner (PTAC): This system is common for small hotels and assumes electric resistance heat. It can be selected for hotels only of any size, or low-rise multifamily.
f. Packaged Terminal Heat Pump (PTHP): This system is common for small hotels, or motels. Heating fuel is electricity via electric-drive heat pumps. It can be selected for hotels only of any size.
g. Distributed 4-pipe fan coil units (FCUs) with electric chiller and electric boiler: This system type assumes a 4-pipe hydronic distribution system serving distributed fan coil units from a central plant with electric-drive chiller and electric resistance boiler. It can be selected for hotels, schools of any size, or mid-rise multifamily.
h. Distributed 4-pipe fan coil units (FCUs) with electric chiller and gas-fired boiler: This system type assumes a 4-pipe hydronic distribution system serving distributed fan coil units from a central plant with electric-drive chiller and gas-fired boiler. It can be selected for hotels, schools of any size, or mid-rise multifamily.
i. Central Ducted VAV with gas-fired reheat: This system represented a centralized, built-up VAV system served by a 4-pipe hydronic systems for heating and cooling. A central plant with electric-drive chiller and gas-fired boiler provides the hydronic cooling and heat. It can be selected for schools or hospitals of any size.
j. Central Ducted VAV with electric resistance reheat: This system represented a centralized, built-up VAV system served by a 4-pipe hydronic systems for heating and cooling. A central plant with electric-drive chiller and anelectric resistance boiler boiler provides the hydronic cooling and heat. It can be selected for schools or hospitals of any size.
k. Other: This selection should be made for any HVAC system types that does not fit into one of the categories listed above. Note that even if this selection is made, savings will be based on simulations that assume one of the system types listed above.
11. Dominant Heating Fuel:This is a pull-down menu input variable. User must select one of the three entries from the pull-down menu – electric, natural gas, or none. This entry will be used in the logic that determines the set of regression equations to be used to estimate heating savings. For hotels and lowrise multifamily, this entry is overridden to electric if the system type chosen is PTAC or PTHP. For offices, this entry is overridden to electric if the system type chosen is Packaged VAV with Electric Reheat. If "none" is selected, savings for heating will be zero.
12. Cooling Installed?: This is a pull-down menu input variable. User must select either "yes" or "no." If "no" is selected, cooling savings for will be adjusted to reflect HVAC auxiliary savings only.
13. Tpe of Existing Window: This is a pull-down menu inpt. User must select one of the two entries from the pull-down menu - single or double. Single represents windows wth single pane clear glass (U-value of 1.04 Btu/hr-SF-F and solar heat gain coefficient (SHGC) of 0.73). Double represents windows with double pane clear glass (U-value of 0.57 Btu/hr-SF-F and SHGC of 0.63).
14. Type of CSW Analyzed: This is a pull-down menu input that is dependent upon the type of existing window selected. User must select one of the two entries from the pull-down menu - single or double. Note that for double pane existing windows, the only selection in single. Single represents single pane CSW product lines, and is the most common type of CSW product in the current market. Savings reported in this calculator for single pane CSW (in combination with single pane primary window) assume that improved window U-value of 0.47 Btu/hr-SF-F and improved window solar heat gain coeefiecient (SHGC) of 0.57. Savings reported in this calculator for single pane CSW (in combination with double pane primary window) assume that improved window U-value of 0.40 Btu/hr-SF-F and improved window solar heat gain coefiecient (SHGC) of 0.47. Double represents double pane CSW product lines. Savings reported in this calculator for double pane CSW (in combination with a single pane primary window) assume that improved window U-value of 0.37 Btu/hr-SF-F and improved window solar heat gain coeefiecient (SHGC) of 0.32. This entry will be used in the logic that determines the set of regression equations to be used to estimate savings.
15. Sq.Ft. of CSW Installed: This is a numerical entry representing the total area, in sq.ft. of CSW units being considered for installation. The input is not limited to a minimum or a maximum value. However, if a value less than zero is input, negative savings will be reported. This is not a relevant answer, therefore a negative number should not be input. If an excessively large number is input that results in an estimated window to wall ratio greater than 50%, a user alert will be generated, “Warning: Sq.Ft of CSW Installed Appears Larger than Practical for this Building Size.”
Special Input Cells: | For offices only: Annual Operating Hours: This is a numerical whole number entry with limits defined. Minimum entry is 1986 hours per year. Maximum entry is 8760 hours per year, representing continuous operation. Entry is the number of HVAC operating hours per year, averaged for the entire building.
For hotels only: Ave. Occupancy Rate: This is a percentage entry that represents that average annual occupancy rate of the hotel. It has implicit limits. Any entry less than 33% will use 33% in the savings logic. Entries above 100% will use 100% in the savings logic. Entries between 33% and 100% will interpolate between minimum and maixmum savings factors.
For schools only: Building Type: This is a pull-down menu selection that allows user to select Primary or Secondary School type.
For multifamily only: Infiltration Savings: This is a pull-down menu selection that allows user to select "Included" or "Excluded". If infiltraton savings is included, then estimated savings includes a benefit associated with reduced perimeter zone infiltration. If excluded, reported savings will be adjusted to reflect savings based only on improved window U-value and SHGC.

## Office
COMMERCIAL SECONDARY WINDOWS SAVINGS CALCULATOR |  |  | Mid-size Office | User Notes / Guidelines / Warnings
Ver. 2.0.0 |  |  | 2025-01-13 | User input notes are indicated by red triangles in select cells. Hover to read on-line help. Detailed input guidelines are provided in the User Documentaiton tab and in the dynamic cells below.
Information About Your Project
Project Name | Example, 250,000 SF, 10-story Office
Project Address | Street | City, State | Zip Code
New York, NY
Contact Information | Name | Phone | Email
Annual Electric Energy Savings, kWh/yr |  |  | 475185.1295
Annual Natural Gas Energy Savings, therms/yr |  |  | 0
Annual Energy Cost Savings, $/year |  |  | 57022.2155
Baseline Energy Use Intensity, kBtu/SF-year |  |  | 130.3729
Savings, % and kBtu/SF-year: |  | 16.59% | 21.6241
Information About Your Building Location |  | Information About Your Building | [10 empty] | 0
|  | Building Type | Office
Project Location (State) | Texas | Building Area, Sq.Ft. | 75000 | Minimum office size limit is approximately 15,000 sq.ft. Maximum office size limit is approximately 500,000 sq.ft.
Project Location (City) | Houston | No. of Floors | 5 | Mid-size offices are typically 3 floors or less in height.
Electric Utility | Con Edison | HVAC System Type | Packaged VAV with electric reheat | For heat pumps, adjustment of electrical heating savings is warranted. See user documentation.
Natural Gas Utility | Con Edison | Heating Fuel | Electric | For packaged VAV options, make sure the fuel type is consistent with the system choice, especially for electric reheat (fuel type=electric.) | [8 empty] | SingleSingleMidOfficePVAV_ElecElectricLo
|  | Cooling Installed? | Yes | Savings includes reduction in mechanical cooling. |  | Lookup Key & Interpolation Factors | [7 empty] | Savings Factors |  |  |  | Clg | Graphics Drivers
Location HDD (Base 65) | 1439 | Annual Operating Hours | 8000 | Minimum input is 1980 hours/yr. Maximum input is 8760 hours/yr. |  | Base | CSW Type | Size | Building Type | HVAC System Type | Fuel | Hours | LU Conc | H, kWh | C, kWh | H, therms | EUI | Factor | EUI |  | Peak Clg Ld
Location CDD (Base 65) | 2974 | Type of Existing Window | Single pane | U-assembly = 1.03 Btu/hr-SF-F; SHGC = 0.73 | Hi | Single | Double | Mid | Office | PVAV_Elec | Electric | 8760 | SingleDoubleMidOfficePVAV_ElecElectric8760 | 22.459 | 20.7471 | 0 | 140.3818 | 1 | 130.3729 | 0 | 170.0046 | 0 | Baseline
|  | Information About Your Proposed CSW Project |  |  | Lo | Single | Double | Mid | Office | PVAV_Elec | Electric | 2912 | SingleDoubleMidOfficePVAV_ElecElectric2912 | 4.5691 | 10.8793 | 0 | 63.3661 |  | 108.7488 | 21.6241 | 103.0762 | 66.9283 | CSW
Information About Your Building |  | Type of CSW Analyzed | Double | Do not select double pane secondary windows added to double pane primary windows. | [14 empty] | % | 0.16586 |  | 0.39369
Electric Rate, $/kWh | 0.12 | Sq.ft. of CSW Installed | 12000 | Typical building Window-Wall Ratio (WWR) is between 0.1-0.5. If unsure about actual CSW Sq.Ft., input CSW area such thatWWR is 0.25.
Natural Gas Rate, $/therm | 1.2 | Est. Window Wall Ratio | 0.3266
Savings Output
Heating, kWh/SFCSW | 20.1341 | Electric Savings, kWh/yr | 475185.1295
Cooling & Fans, kWh/SFCSW | 19.4647
Heating, therms/SFcSW | 0 | Gas Savings, therms/yr | 0
Electric Cost Savings, $/yr | 57022.2155 | Total Savings, kBtu/SF-yr | 21.6241
Gas Cost Savings, $/yr | 0 | Total Savings, $/yr | 57022.2155
Annual Percentage Total Energy Savings |  |  | 16.59%
Percentage HVAC Downsize |  |  | 39.37%
Note on C4: Identify individual project name and/or calculation run.
Note on C18: Select appropriate state from list of U.S. states.
Note on F18: Enter the area of the building that is heated or cooled.
Note on C19: Select city that is closest (geographically) to project location.
Note on F19: Enter number of floors contributing to building area entry including basement floors.
Note on C20: Enter name of servicing electric utility.
Note on F20: Select the HVAC system type that best matches predominant system type.
Note on C21: Enter name of servicing electric utility.
Note on F21: Insert predominant heating fuel. For electric resistance reheat systems, select "electric."
Note on F22: Select "No" if there is no cooling system installed.
Note on F23: Enter average annual operating hours for HVAC system. Include hours that system operates at night or in other unoccupied periods.
Note on F24: Enter dominant type of existnig window
Note on F26: Select type of CSW system proposed for installation. Single=single pane CSW. Double=double pane CSW.
Note on C27: Input melded rate, $/kWh that includes both energy (kWh) charge and demand (kW) charge.
Note on F27: Enter the sq.ft. of CSW units proposed to be installed in the building. Include all units in a total figure.
Note on C28: Enter average annual gas rate, in $/therm. If the building does not heat with gas, enter zero.

## Hotel
COMMERCIAL SECONDARY WINDOWS SAVINGS CALCULATOR |  |  | Large Hotel | User Notes / Guidelines / Warnings
Ver. 2.0.0 |  |  | 2025-01-13 | User input notes are indicated by red triangles in select cells. Hover to read on-line help. Detailed input guidelines are provided in the User Documentaiton tab and in the dynamic cells below.
Information About Your Project
Project Name | Royal Hawaiian Example
Project Address | Street | City, State | Zip Code
Honolulu HI
Contact Information | Name | Phone | Email
Annual Electric Energy Savings, kWh/yr |  |  | 145759.26
Annual Natural Gas Energy Savings, therms/yr |  |  | 54.946
Annual Energy Cost Savings, $/year |  |  | 55388.5188
Baseline Energy Use Intensity, kBtu/SF-year |  |  | 117.6789
Savings, % and kBtu/SF-year |  | 21.37% | 25.1485
Information About Your Building Location |  | Information About Your Building | [11 empty] | 0
|  | Building Type | Large Hotel
Project Location (State) | Hawaii | Building Area, Sq.Ft. | 20000 | Minimum small hotel size limit is approximately 15,000 sq.ft. Maximum size limit is approximately 250,000 sq.ft.
Project Location (City) | Honolulu | No. of Floors | 2
Electric Utility | Hawaiian Electric | HVAC System Type | Fan Coil Unit | PTAC or PTHP choice will default to Small Hotel regardless of building area input. Fan Coil Unit or Other choice will default to large hotel regardless of building area input.
Natural Gas Utility | N/A | Dominant Heating Fuel | Natural Gas | User can select either Electric or Natural Gas as fuel type. Select None if the building does not have installed heating.
|  | Cooling Installed? | Yes | Savings includes reduction in mechanical cooling. |  | Lookup Key & Interpolation Factors | [8 empty] | Savings Factors |  |  |  | Clg | Graphics Drivers
Location HDD (Base 65) | 0 | Ave. Occupancy Rate | 100% | Typical occupancy rate is between 50% to 100%. For savings estimates, occupancy rates between 33% and 100% are used. |  | Base | CSW Type | Size | Building Type | HVAC System Type | Fuel | PTHP HDD | Occ | LU Conc | H, kWh | C, kWh | H, therms | EUI | Factor | EUI |  | Peak Clg Ld
Location CDD (Base 65) | 4561 | Type of Existing Window | Single pane | U-assembly = 1.03 Btu/hr-SF-F; SHGC = 0.73 | High | Single | Double | Large | Hotel | FCU | Natural Gas |  | 100 | SingleDoubleLargeHotelFCUNatural Gas100 | 0 | 9.7173 | 0.0036631 | 117.6789 | 1 | 117.6789 | 0 | 61.7605 | 0 | Baseline
|  | Information About Your Proposed CSW Project |  |  | Low | Single | Double | Large | Hotel | FCU | Natural Gas |  | 33 | SingleDoubleLargeHotelFCUNatural Gas33 | 0 | 8.0174 | 0.0028885 | 111.2992 |  | 92.5304 | 25.1485 | -171.6401 | 233.4006 | CSW
Information About Your Building |  | Type of CSW Analyzed | Double | Do not select double pane secondary windows added to double pane primary windows. | [15 empty] | % | 0.2137 |  | 3.7791
Electric Rate, $/kWh | 0.38 | Sq.ft. of CSW Installed | 15000 | WARNING: Sq.Ft of CSW Installed Appears Larger than Practical for this Building Size. Typical window to window to wall ratio is 0.1 to 0.5
Natural Gas Rate, $/therm | 0 | Est. Window Wall Ratio | 1.25
Savings Output
Heating, kWh/SFCSW | 0 | Electric Savings, kWh/yr | 145759.26
Cooling & Fans, kWh/SFCSW | 9.7173
Heating, therms/SFCSW | 0.0036631 | Gas Savings, therms/yr | 54.946
Electric Cost Savings, $/yr | 55388.5188 | Total Savings, kBtu/SF-yr | 25.1485
Gas Cost Savings, $/yr | 0 | Total Savings, $/yr | 55388.5188
Annual Percentage Total Energy Savings |  |  | 21.37%
Percentage HVAC Downsize |  |  | 377.9%
Note on C4: Identify individual project name and/or calculation run.
Note on C18: Select appropriate state from list of U.S states.
Note on F18: Enter the area of the building that is heated or cooled.
Note on C19: Select city that is closest (geographically) to project location.
Note on F19: Enter number of floors contributing to building area entry excluding basement floors.
Note on C20: Enter name of servicing electric utility.
Note on F20: Select the HVAC system type that best matches predominant system type.
Note on C21: Enter name of servicing gas utility, if any.
Note on F21: Insert predominant heating fuel. For electric resistance or heat pump systems, select "electric."
Note on F22: For electric resistance heating only systems, select "No."
Note on F23: Enter average annual occupancy rate.
Note on F24: Enter dominant type of existnig window
Note on F26: Select type of CSW system proposed for installation. Single=single pane CSW. Double=double pane CSW.
Note on C27: Input melded rate, $/kWh that includes both energy (kWh) charge and demand (kW) charge.
Note on F27: Enter the sq.ft. of CSW units proposed to be installed in the building. Include all units in a total figure.
Note on C28: Enter average annual gas rate, in $/therm. If the building does not heat with gas, enter zero.

## School
COMMERCIAL SECONDARY WINDOWS SAVINGS CALCULATOR |  |  | Secondary School | User Notes / Guidelines / Warnings
Ver. 2.0.0 |  |  | 2025-01-13 | User input notes are indicated by red triangles in select cells. Hover to read on-line help. Detailed input guidelines are provided in the User Documentaiton tab and in the dynamic cells below.
Information About Your Project
Project Name | 300000 SF High School Example
Project Address | Street | City, State | Zip Code
Salt Lake City UT
Contact Information | Name | Phone | Email
Annual Electric Energy Savings, kWh/yr |  |  | 43338.6167
Annual Natural Gas Energy Savings, therms/yr |  |  | 5153.6814
Annual Energy Cost Savings, $/year |  |  | 5259.1397
Baseline Energy Use Intensity, kBtu/SF-year |  |  | 82.2746
Savings, % and kBtu/SF-year |  | 10.08% | 8.291
Information About Your Building Location |  | Information About Your Building | [9 empty] | 0
|  | Building Type | Secondary School | Select school type - primary (elementary) or secondary (middle or high school).
Project Location (State) | Utah | Building Area, Sq.Ft. | 80000 | Minimum school size limit is approximately 25,000 sq.ft. Maximum size limit is approximately 350,000 sq.ft.
Project Location (City) | Salt Lake City | No. of Floors | 2
Electric Utility | Rocky Mountain Power | HVAC System Type | Central Ducted VAV | For heat pumps, adjustment of electrical heating savings is warranted. See user documentation.
Natural Gas Utility | Enbridge Gas | Dominant Heating Fuel | Natural Gas
|  | Cooling Installed? | Yes |  | Lookup Key | [7 empty] | Savings Factors |  |  | Clg | Graphics Drivers
Location HDD (Base 65) | 5350 | Type of Existing Window | Double pane | U-assembly = 0.57 Btu/hr-SF-F; SHGC = 0.63 | Base | CSW Type | Building Type | HVAC System Type | Fuel | Location | Occ | LU Conc | H, kWh | C, kWh | H, therms | Factor | EUI |  | Peak Clg Ld
Location CDD (Base 65) | 1118 |  |  |  | Double | Single | SS | VAV | Natural Gas |  |  | DoubleSingleSSVAVNatural Gas | 0 | 4.3339 | 0.51537 | 1 | 82.2746 | 0 | 115.0505 | 0 | Baseline
|  | Information About Your Proposed CSW Project | [14 empty] | 73.9836 | 8.291 | 101.9868 | 13.0637 | CSW
Information About Your Building |  | Type of CSW Analyzed | Single | Double pane secondary windows are a valid entry only for buildings with existing single pane windows. | [12 empty] | % | 0.10077 |  | 0.11355
Electric Rate, $/kWh | 0.05 | Sq.ft. of CSW Installed | 10000 | Typical building Window-Wall Ratio (WWR) is between 0.1-0.5. If unsure about actual CSW Sq.Ft., input CSW area such thatWWR is 0.25.
Natural Gas Rate, $/therm | 0.6 | Est. Window Wall Ratio | 0.41667
Savings Output
Heating, kWh/SFCSW | 0 | Electric Savings, kWh/yr | 43338.6167
Cooling & Fans, kWh/SFCSW | 4.3339
Heating, therms/SFCSW | 0.51537 | Gas Savings, therms/yr | 5153.6814
Electric Cost Savings, $/yr | 2166.9308 | Total Savings, kBtu/SF-yr | 8.291
Gas Cost Savings, $/yr | 3092.2089 | Total Savings, $/yr | 5259.1397
Annual Percentage Total Energy Savings |  |  | 10.08%
Percentage HVAC Downsize |  |  | 11.35%
Note on C4: Identify individual project name and/or calculation run.
Note on F17: Select school type.
Note on C18: Select appropriate state from list of Pacific Northwest states.
Note on F18: Enter the area of the building that is heated or cooled.
Note on C19: Select city that is closest (geographically) to project location.
Note on F19: Enter number of floors contributing to building area entry excluding basement floors.
Note on C20: Enter name of servicing electric utility.
Note on F20: Select the HVAC system type that best matches predominant system type.
Note on C21: Enter name of servicing gas utility, if any.
Note on F21: Insert predominant heating fuel. For electric resistance reheat systems, select "electric."
Note on F23: Enter dominant type of existnig window
Note on F26: Select type of CSW system proposed for installation. Single=single pane CSW. Double=double pane CSW.
Note on C27: Input melded rate, $/kWh that includes both energy (kWh) charge and demand (kW) charge.
Note on F27: Enter the sq.ft. of CSW units proposed to be installed in the building. Include all units in a total figure.
Note on C28: Enter average annual gas rate, in $/therm. If the building does not heat with gas, enter zero.

## Hospital
COMMERCIAL SECONDARY WINDOWS SAVINGS CALCULATOR |  |  | Hospital | User Notes / Guidelines / Warnings
Ver. 2.0.0 |  |  | 2025-01-13 | User input notes are indicated by red triangles in select cells. Hover to read on-line help. Detailed input guidelines are provided in the User Documentaiton tab and in the dynamic cells below.
Information About Your Project
Project Name | Small Hospital Example
Project Address | Street | City, State | Zip Code
Walla Walla WA
Contact Information | Name | Phone | Email
Annual Electric Energy Savings, kWh/yr |  |  | 188469.3571
Annual Natural Gas Energy Savings, therms/yr |  |  | 18037.5776
Annual Energy Cost Savings, $/year |  |  | 27483.0092
Baseline Energy Use Intensity, kBtu/SF-year |  |  | 230.1992
Savings, % and kBtu/SF-year |  | 5.062% | 11.6524
Information About Your Building Location |  | Information About Your Building
|  | Building Type | Hospital
Project Location (State) | Washington | Building Area, Sq.Ft. | 210000 | Minimum size limit for small hospital is approximately 30,000 sq.ft. Maximum size limit is approximately 300,000 sq.ft.
Project Location (City) | Walla Walla | No. of Floors | 4
Electric Utility | Pacific Power | HVAC System Type | Central Ducted VAV | For heat pumps, adjustment of electrical heating savings is warranted. See user documentation.
Natural Gas Utility | NWN | Dominant Heating Fuel | Natural Gas
|  | Cooling Installed? | Yes |  | Lookup Key | [7 empty] | Savings Factors |  |  | Clg | Graphics Drivers
Location HDD (Base 65) | 4836 | Type of Existing Window | Single pane | U-assembly = 1.03 Btu/hr-SF-F; SHGC = 0.73 | Base | CSW Type | Building Type | HVAC System Type | Fuel | Location | Occ | LU Conc | H, kWh | C, kWh | H, therms | Factor | EUI |  | Peak Clg Ld
Location CDD (Base 65) | 839 |  |  |  | Single | Double | Hosp | VAV | Natural Gas |  |  | SingleDoubleHospVAVNatural Gas | 0 | 15.7058 | 1.5031 | 1 | 230.1992 | 0 | 365.1315 | 0 | Baseline
|  | Information About Your ProposedCSW Project | [14 empty] | 218.5468 | 11.6524 | 340.8423 | 24.2892 | CSW
Information About Your Building |  | Type of CSW Analyzed | Double | Double pane secondary windows are a valid entry only for buildings with existing single pane windows. | [12 empty] | % | 0.050619 |  | 0.066522
Electric Rate, $/kWh | 0.075 | Sq.ft. of CSW Installed | 12000 | Typical building Window-Wall Ratio (WWR) is between 0.1-0.5. If unsure about actual CSW Sq.Ft., input CSW area such thatWWR is 0.25.
Natural Gas Rate, $/therm | 0.74 | Est. Window Wall Ratio | 0.21822
Savings Output
Heating, kWh/SFCSW | 0 | Electric Savings, kWh/yr | 188469.3571
Cooling & Fans, kWh/SFCSW | 15.7058
Heating, therms/SFCSW | 1.5031 | Gas Savings, therms/yr | 18037.5776
Electric Cost Savings, $/yr | 14135.2018 | Total Savings, kBtu/SF-yr | 11.6524
Gas Cost Savings, $/yr | 13347.8074 | Total Savings, $/yr | 27483.0092
Annual Percentage Total Energy Savings |  |  | 5.062%
Percentage HVAC Downsize |  |  | 6.652%
Note on C4: Identify individual project name and/or calculation run.
Note on C18: Select appropriate state from list of Pacific Northwest states.
Note on F18: Enter the area of the building that is heated or cooled.
Note on C19: Select city that is closest (geographically) to project location.
Note on F19: Enter number of floors contributing to building area entry excluding basement floors.
Note on C20: Enter name of servicing electric utility.
Note on F20: Select the HVAC system type that best matches predominant system type.
Note on C21: Enter name of servicing gas utility, if any.
Note on F21: Insert predominant heating fuel. For electric resistance reheat systems, select "electric."
Note on F23: Enter dominant type of existnig window
Note on F26: Select type of CSW system proposed for installation. Single=single pane CSW. Double=double pane CSW.
Note on C27: Input melded rate, $/kWh that includes both energy (kWh) charge and demand (kW) charge.
Note on F27: Enter the sq.ft. of CSW units proposed to be installed in the building. Include all units in a total figure.
Note on C28: Enter average annual gas rate, in $/therm. If the building does not heat with gas, enter zero.

## Multi-family
COMMERCIAL SECONDARY WINDOWS SAVINGS CALCULATOR |  |  | Mid-rise Multifamily | User Notes / Guidelines / Warnings
Ver. 2.0.0 |  |  | 2025-01-13 | User input notes are indicated by red triangles in select cells. Hover to read on-line help. Detailed input guidelines are provided in the User Documentaiton tab and in the dynamic cells below.
Information About Your Project
Project Name | Low Rise Apartment Example
Project Address | Street | City, State | Zip Code
Raliegh NC
Contact Information | Name | Phone | Email
Annual Electric Energy Savings, kWh/yr |  |  | 128179.389
Annual Natural Gas Energy Savings, therms/yr |  |  | 0
Annual Energy Cost Savings, $/year |  |  | 21790.4961
Baseline Energy Use Intensity, kBtu/SF-year |  |  | 8.095
Savings, % and kBtu/SF-year |  | 11.53% | 4.8608
Information About Your Building Location |  | Information About Your Building | [9 empty] | 0
|  | Building Type | Mid-rise Multifamily
Project Location (State) | North_Carolina | Building Area, Sq.Ft. | 90000 | Minimum multi-family size limit is approximately 10,000 sq.ft. Maximum size limit is approximately 150,000 sq.ft.
Project Location (City) | Raleigh | No. of Floors | 5 | Mid-size multi-family buildings are designated for all buildings 4 floors and above.
Electric Utility | Duke Energy | HVAC System Type | Fan Coil Unit | Savings estimated for Low-rise assume Packaged terminal air conditioner (PTAC) system. Savings for Mid-rise assume Fan coil unit (FCU) system.")
Natural Gas Utility | N/A | Dominant Heating Fuel | Electric | [13 empty] | Heat | Cool
|  | Cooling Installed? | Yes | Savings includes reduction in mechanical cooling. |  | Lookup Key & Interpolation Factors | [6 empty] | Savings Factors |  |  |  | Infil | Infil | Clg | Graphics Drivers
Location HDD (Base 65) | 3465 | Type of Existing Window | Single pane | U-assembly = 1.03 Btu/hr-SF-F; SHGC = 0.73 |  | Base | CSW Type | Size | Building Type | HVAC System Type | Fuel | LU Conc | H, kWh | C, kWh | H, therms | EUI | Factor | Factor | Factor | EUI |  | Peak Clg Ld
Location CDD (Base 65) | 1566 | Infiltration Savings | Included | Savings includes contribution of reduced air leakage.
[5 empty] | High | Single | Single | Mid | MF | FCU | Electric | SingleSingleMidMFFCUElectric | 8.095 | 4.7229 | 0 | 42.1565 | 1 | 1 | 1 | 42.1565 | 0 | 106.0001 | 0 | Baseline
|  | Information About Your Proposed CSW Project | [17 empty] | 37.2956 | 4.8608 | 85.8878 | 20.1123 | CSW
Information About Your Building |  | Type of CSW Analyzed | Single | Do not select double pane secondary windows added to double pane primary windows. | [15 empty] | % | 0.1153 |  | 0.18974
Electric Rate, $/kWh | 0.17 | Sq.ft. of CSW Installed | 10000 | Typical building Window-Wall Ratio (WWR) is between 0.1-0.5. If unsure about actual CSW Sq.Ft., input CSW area such that WWR is 0.25.
Natural Gas Rate, $/therm | 0 | Est. Window Wall Ratio | 0.24845
Savings Output
Heating, kWh/SFCSW | 8.095 | Electric Savings, kWh/yr | 128179.389
Cooling & Fans, kWh/SFCSW | 4.7229
Heating, therms/SFCSW | 0 | Gas Savings, therms/yr | 0
Electric Cost Savings, $/yr | 21790.4961 | Total Savings, kBtu/SF-yr | 4.8608
Gas Cost Savings, $/yr | 0 | Total Savings, $/yr | 21790.4961
Annual Percentage Total Energy Savings |  |  | 11.53%
200
Percentage HVAC Downsize |  |  | 18.97%
Note on C4: Identify individual project name and/or calculation run.
Note on C18: Select appropriate state from list of U.S. states.
Note on F18: Enter the area of the building that is heated or cooled.
Note on C19: Select city that is closest (geographically) to project location.
Note on F19: Enter number of floors contributing to building area entry excluding basement floors.
Note on C20: Enter name of servicing electric utility.
Note on F20: Select the HVAC system type that best matches predominant system type.
Note on C21: Enter name of servicing gas utility, if any.
Note on F21: Insert predominant heating fuel. For electric resistance heat including PTAC systems, select "electric."
Note on F23: Enter the dominent type of existing window.
Note on F24: Indicate whether savings due to reduced infiltration is to be included.
Note on F27: Select type of CSW system proposed for installation. Single=single pane CSW. Double=double pane CSW.
Note on C28: Input melded rate, $/kWh that includes both energy (kWh) charge and demand (kW) charge.
Note on F28: Enter the sq.ft. of CSW units proposed to be installed in the building. Include all units in a total figure.
Note on C29: Enter average annual gas rate, in $/therm. If the building does not heat with gas, enter zero.

## Savings Lookup
Savings Look-up Tables (using Regression Equations with HDD/CDD as independent variables)
[9 empty] | Savings |  |  |  |  | EUI |  |  |  | Loads | Loads
[9 empty] | Electric Savings, kWh/SF |  | Gas Savings, therms/SF |  | Regression_Done | Base_EUI | CSW_EUI | Percent | Regression_Done | Baseline Peak Cooling | Clg Load Reduced | Htg Load Reduced | Baseline Peak Cooling | Base Clg Load | CSW Ld Red | CSW Ld Red | CWS Clg Load | Regression_done | Infil Savings Reduction Factors |  | Cool Adjust
Base | CSW_Type | Building_Size | Building_Type | HVAC_System_Type | Fuel_Type | PTHP | Hours | Look-up_Conc | Electric_savings_Heat_kWhperSF | electric_savings_Cooling_and_Aux_kWhperSF | Gas_savings_Heat_thermsperSF |  |  | Base_EUI_kBtuperSFperyr | CSW_EUI_kBtuperSFperyr | Percent | Regression_Done | baseline_peak_cooling_BtuhperSF | Clg_Load_reduced_BtuhperSF | htg_load_reduced_BtuhperSF | baseline_peak_cooling_Btuh | base_cooling_load_Tons | CSW_ld_red_Btuh | csw_ld_red_Tons | CWS_Clg_load_Tons |  | infiltration_savings_reduction_factors_Heat | infiltration_reduction_factors_Cool | Cool_adjust
Single | Single | Mid | Office | PVAV_Elec | Electric |  | 2080 | SingleSingleMidOfficePVAV_ElecElectric2080 | 3.1617 | 3.9914 | 0 |  | Y | 51.9448 | 30.3207 | 41.63% | Y | 27.2007 | 34.168 |  | 2040054.7293 | 170.0046 | 410016.4792 | 34.168 | 135.8365 | Y |  |  | 0.52708
Single | Single | Mid | Office | PVAV_Elec | Electric |  | 2912 | SingleSingleMidOfficePVAV_ElecElectric2912 | 4.8351 | 6.6063 | 0 |  | Y | 63.3661 | 41.742 | 34.13% | Y | 27.2007 | 34.168 |  | 2040054.7293 | 170.0046 | 410016.4792 | 34.168 | 135.8365 | Y |  |  | 0.52708
Single | Single | Mid | Office | PVAV_Elec | Electric |  | 8760 | SingleSingleMidOfficePVAV_ElecElectric8760 | 19.5673 | 15.9503 | 0 |  | Y | 140.3818 | 118.7577 | 15.4% | Y | 27.2007 | 34.168 |  | 2040054.7293 | 170.0046 | 410016.4792 | 34.168 | 135.8365 | Y |  |  | 0.52708
Single | Double | Mid | Office | PVAV_Elec | Electric |  | 2080 | SingleDoubleMidOfficePVAV_ElecElectric2080 | 3.0118 | 6.7588 | 0 |  | Y | 51.9448 | 30.3207 | 41.63% | Y | 27.2007 | 66.9283 |  | 2040054.7293 | 170.0046 | 803140.0342 | 66.9283 | 103.0762 | Y |  |  | 0.52708
Single | Double | Mid | Office | PVAV_Elec | Electric |  | 2912 | SingleDoubleMidOfficePVAV_ElecElectric2912 | 4.5691 | 10.8793 | 0 |  | Y | 63.3661 | 41.742 | 34.13% | Y | 27.2007 | 66.9283 |  | 2040054.7293 | 170.0046 | 803140.0342 | 66.9283 | 103.0762 | Y |  |  | 0.52708
Single | Double | Mid | Office | PVAV_Elec | Electric |  | 8760 | SingleDoubleMidOfficePVAV_ElecElectric8760 | 22.459 | 20.7471 | 0 |  | Y | 140.3818 | 118.7577 | 15.4% | Y | 27.2007 | 66.9283 |  | 2040054.7293 | 170.0046 | 803140.0342 | 66.9283 | 103.0762 | Y |  |  | 0.52708
Double | Single | Mid | Office | PVAV_Elec | Electric |  | 2080 | DoubleSingleMidOfficePVAV_ElecElectric2080 | 1.4328 | 3.0676 | 0 |  | Y | 52.0337 | 30.4096 | 41.56% | Y | 24.0315 | 23.1953 |  | 1802361.3644 | 150.1968 | 278343.7327 | 23.1953 | 127.0015 | Y |  |  | 0.52708
Double | Single | Mid | Office | PVAV_Elec | Electric |  | 2912 | DoubleSingleMidOfficePVAV_ElecElectric2912 | 2.0904 | 5.196 | 0 |  | Y | 60.0297 | 38.4056 | 36.02% | Y | 24.0315 | 23.1953 |  | 1802361.3644 | 150.1968 | 278343.7327 | 23.1953 | 127.0015 | Y |  |  | 0.52708
Double | Single | Mid | Office | PVAV_Elec | Electric |  | 8760 | DoubleSingleMidOfficePVAV_ElecElectric8760 | 11.1731 | 9.5612 | 0 |  | Y | 123.8016 | 102.1775 | 17.47% | Y | 24.0315 | 23.1953 |  | 1802361.3644 | 150.1968 | 278343.7327 | 23.1953 | 127.0015 | Y |  |  | 0.52708
Single | Single | Mid | Office | PVAV_Gas | Natural Gas |  | 2080 | SingleSingleMidOfficePVAV_GasNatural Gas2080 | 0 | 3.9914 | 0.15459 |  | Y | 56.6503 | 35.0262 | 38.17% | Y | 27.2007 | 34.168 |  | 2040054.7293 | 170.0046 | 410016.4792 | 34.168 | 135.8365 | Y |  |  | 0.52708
Single | Single | Mid | Office | PVAV_Gas | Natural Gas |  | 2912 | SingleSingleMidOfficePVAV_GasNatural Gas2912 | 0 | 6.6063 | 0.23624 |  | Y | 70.2793 | 48.6552 | 30.77% | Y | 27.2007 | 34.168 |  | 2040054.7293 | 170.0046 | 410016.4792 | 34.168 | 135.8365 | Y |  |  | 0.52708
Single | Single | Mid | Office | PVAV_Gas | Natural Gas |  | 8760 | SingleSingleMidOfficePVAV_GasNatural Gas8760 | 0 | 15.9503 | 0.5951 |  | Y | 156.6181 | 134.994 | 13.81% | Y | 27.2007 | 34.168 |  | 2040054.7293 | 170.0046 | 410016.4792 | 34.168 | 135.8365 | Y |  |  | 0.52708
Single | Double | Mid | Office | PVAV_Gas | Natural Gas |  | 2080 | SingleDoubleMidOfficePVAV_GasNatural Gas2080 | 0 | 6.7588 | 0.14614 |  | Y | 56.6503 | 35.0262 | 38.17% | Y | 27.2007 | 66.9283 |  | 2040054.7293 | 170.0046 | 803140.0342 | 66.9283 | 103.0762 | Y |  |  | 0.52708
Single | Double | Mid | Office | PVAV_Gas | Natural Gas |  | 2912 | SingleDoubleMidOfficePVAV_GasNatural Gas2912 | 0 | 10.8793 | 0.22239 |  | Y | 70.2793 | 48.6552 | 30.77% | Y | 27.2007 | 66.9283 |  | 2040054.7293 | 170.0046 | 803140.0342 | 66.9283 | 103.0762 | Y |  |  | 0.52708
Single | Double | Mid | Office | PVAV_Gas | Natural Gas |  | 8760 | SingleDoubleMidOfficePVAV_GasNatural Gas8760 | 0 | 20.7471 | 1.0933 |  | Y | 156.6181 | 134.994 | 13.81% | Y | 27.2007 | 66.9283 |  | 2040054.7293 | 170.0046 | 803140.0342 | 66.9283 | 103.0762 | Y |  |  | 0.52708
Double | Single | Mid | Office | PVAV_Gas | Natural Gas |  | 2080 | DoubleSingleMidOfficePVAV_GasNatural Gas2080 | 0 | 3.0676 | 0.069481 |  | Y | 53.8731 | 32.249 | 40.14% | Y | 24.0315 | 23.1953 |  | 1802361.3644 | 150.1968 | 278343.7327 | 23.1953 | 127.0015 | Y |  |  | 0.52708
Double | Single | Mid | Office | PVAV_Gas | Natural Gas |  | 2912 | DoubleSingleMidOfficePVAV_GasNatural Gas2912 | 0 | 5.196 | 0.10127 |  | Y | 63.1385 | 41.5144 | 34.25% | Y | 24.0315 | 23.1953 |  | 1802361.3644 | 150.1968 | 278343.7327 | 23.1953 | 127.0015 | Y |  |  | 0.52708
Double | Single | Mid | Office | PVAV_Gas | Natural Gas |  | 8760 | DoubleSingleMidOfficePVAV_GasNatural Gas8760 | 0 | 9.5612 | 0.54301 |  | Y | 127.1656 | 105.5415 | 17% | Y | 24.0315 | 23.1953 |  | 1802361.3644 | 150.1968 | 278343.7327 | 23.1953 | 127.0015 | Y |  |  | 0.52708
Single | Single | Large | Office | VAV | Electric |  | 2080 | SingleSingleLargeOfficeVAVElectric2080 | 3.5131 | 4.5087 | 0 |  | Y | 52.9052 | 31.2811 | 40.87% | Y | 29.6579 | 13.2347 |  | 2224339.5371 | 185.3616 | 158816.7352 | 13.2347 | 172.1269 | Y |  |  | 0.69813
Single | Single | Large | Office | VAV | Electric |  | 2912 | SingleSingleLargeOfficeVAVElectric2912 | 5.3574 | 7.468 | 0 |  | Y | 81.6305 | 60.0064 | 26.49% | Y | 29.6579 | 13.2347 |  | 2224339.5371 | 185.3616 | 158816.7352 | 13.2347 | 172.1269 | Y |  |  | 0.69813
Single | Single | Large | Office | VAV | Electric |  | 8760 | SingleSingleLargeOfficeVAVElectric8760 | 21.673 | 18.02 | 0 |  | Y | 141.237 | 119.6129 | 15.31% | Y | 29.6579 | 13.2347 |  | 2224339.5371 | 185.3616 | 158816.7352 | 13.2347 | 172.1269 | Y |  |  | 0.69813
Single | Double | Large | Office | VAV | Electric |  | 2080 | SingleDoubleLargeOfficeVAVElectric2080 | 3.3518 | 7.6661 | 0 |  | Y | 52.9052 | 31.2811 | 40.87% | Y | 29.6579 | 71.0613 |  | 2224339.5371 | 185.3616 | 852735.8278 | 71.0613 | 114.3003 | Y |  |  | 0.69813
Single | Double | Large | Office | VAV | Electric |  | 2912 | SingleDoubleLargeOfficeVAVElectric2912 | 5.0832 | 12.3303 | 0 |  | Y | 81.6305 | 60.0064 | 26.49% | Y | 29.6579 | 71.0613 |  | 2224339.5371 | 185.3616 | 852735.8278 | 71.0613 | 114.3003 | Y |  |  | 0.69813
Single | Double | Large | Office | VAV | Electric |  | 8760 | SingleDoubleLargeOfficeVAVElectric8760 | 24.9318 | 23.4538 | 0 |  | Y | 141.237 | 119.6129 | 15.31% | Y | 29.6579 | 71.0613 |  | 2224339.5371 | 185.3616 | 852735.8278 | 71.0613 | 114.3003 | Y |  |  | 0.69813
Double | Single | Large | Office | VAV | Electric |  | 2080 | DoubleSingleLargeOfficeVAVElectric2080 | 1.5943 | 3.4508 | 0 |  | Y | 69.6142 | 47.9901 | 31.06% | Y | 27.0809 | 25.7883 |  | 2031066.5382 | 169.2555 | 309459.3862 | 25.7883 | 143.4673 | Y |  |  | 0.69813
Double | Single | Large | Office | VAV | Electric |  | 2912 | DoubleSingleLargeOfficeVAVElectric2912 | 2.3276 | 5.8698 | 0 |  | Y | 78.5544 | 56.9303 | 27.53% | Y | 27.0809 | 25.7883 |  | 2031066.5382 | 169.2555 | 309459.3862 | 25.7883 | 143.4673 | Y |  |  | 0.69813
Double | Single | Large | Office | VAV | Electric |  | 8760 | DoubleSingleLargeOfficeVAVElectric8760 | 12.3807 | 10.8025 | 0 |  | Y | 131.7139 | 110.0898 | 16.42% | Y | 27.0809 | 25.7883 |  | 2031066.5382 | 169.2555 | 309459.3862 | 25.7883 | 143.4673 | Y |  |  | 0.69813
Single | Single | Large | Office | VAV | Natural Gas |  | 2080 | SingleSingleLargeOfficeVAVNatural Gas2080 | 0 | 4.5087 | 0.17124 |  | Y | 54.6768 | 33.0527 | 39.55% | Y | 29.6579 | 13.2347 |  | 2224339.5371 | 185.3616 | 158816.7352 | 13.2347 | 172.1269 | Y |  |  | 0.69813
Single | Single | Large | Office | VAV | Natural Gas |  | 2912 | SingleSingleLargeOfficeVAVNatural Gas2912 | 0 | 7.468 | 0.26159 |  | Y | 86.0717 | 64.4476 | 25.12% | Y | 29.6579 | 13.2347 |  | 2224339.5371 | 185.3616 | 158816.7352 | 13.2347 | 172.1269 | Y |  |  | 0.69813
Single | Single | Large | Office | VAV | Natural Gas |  | 8760 | SingleSingleLargeOfficeVAVNatural Gas8760 | 0 | 18.02 | 1.0568 |  | Y | 147.4517 | 125.8276 | 14.67% | Y | 29.6579 | 13.2347 |  | 2224339.5371 | 185.3616 | 158816.7352 | 13.2347 | 172.1269 | Y |  |  | 0.69813
Single | Double | Large | Office | VAV | Natural Gas |  | 2080 | SingleDoubleLargeOfficeVAVNatural Gas2080 | 0 | 7.6661 | 0.1622 |  | Y | 54.6768 | 33.0527 | 39.55% | Y | 29.6579 | 71.0613 |  | 2224339.5371 | 185.3616 | 852735.8278 | 71.0613 | 114.3003 | Y |  |  | 0.69813
Single | Double | Large | Office | VAV | Natural Gas |  | 2912 | SingleDoubleLargeOfficeVAVNatural Gas2912 | 0 | 12.3303 | 0.24485 |  | Y | 86.0717 | 64.4476 | 25.12% | Y | 29.6579 | 71.0613 |  | 2224339.5371 | 185.3616 | 852735.8278 | 71.0613 | 114.3003 | Y |  |  | 0.69813
Single | Double | Large | Office | VAV | Natural Gas |  | 8760 | SingleDoubleLargeOfficeVAVNatural Gas8760 | 0 | 23.4538 | 1.216 |  | Y | 147.4517 | 125.8276 | 14.67% | Y | 29.6579 | 71.0613 |  | 2224339.5371 | 185.3616 | 852735.8278 | 71.0613 | 114.3003 | Y |  |  | 0.69813
Double | Single | Large | Office | VAV | Natural Gas |  | 2080 | DoubleSingleLargeOfficeVAVNatural Gas2080 | 0 | 3.4508 | 0.077281 |  | Y | 55.4323 | 33.8082 | 39.01% | Y | 27.0809 | 25.7883 |  | 2031066.5382 | 169.2555 | 309459.3862 | 25.7883 | 143.4673 | Y |  |  | 0.69813
Double | Single | Large | Office | VAV | Natural Gas |  | 2912 | DoubleSingleLargeOfficeVAVNatural Gas2912 | 0 | 5.8698 | 0.11292 |  | Y | 82.8414 | 61.2173 | 26.1% | Y | 27.0809 | 25.7883 |  | 2031066.5382 | 169.2555 | 309459.3862 | 25.7883 | 143.4673 | Y |  |  | 0.69813
Double | Single | Large | Office | VAV | Natural Gas |  | 8760 | DoubleSingleLargeOfficeVAVNatural Gas8760 | 0 | 10.8025 | 0.60068 |  | Y | 139.3157 | 117.6916 | 15.52% | Y | 27.0809 | 25.7883 |  | 2031066.5382 | 169.2555 | 309459.3862 | 25.7883 | 143.4673 | Y |  |  | 0.69813
Single | Single | Small | Hotel | PTAC | Electric |  | 33 | SingleSingleSmallHotelPTACElectric33 | 0.26195 | 6.0461 | 0 | 0.033529 | Y | 53.3842 | 28.2357 | 47.11% | Y | 28.4047 | 29.6018 |  | 568094.5753 | 47.3412 | 444027.4853 | 37.0023 | 10.3389 | Y |  |  | #REF!
Single | Single | Small | Hotel | PTAC | Electric |  | 100 | SingleSingleSmallHotelPTACElectric100 | 0.34628 | 7.2822 | 0 | 0.033529 | Y | 61.7548 | 36.6062 | 40.72% | Y | 28.4047 | 29.6018 |  | 568094.5753 | 47.3412 | 444027.4853 | 37.0023 | 10.3389 | Y |  |  | #REF!
Single | Double | Small | Hotel | PTAC | Electric |  | 33 | SingleDoubleSmallHotelPTACElectric33 | 0.33832 | 11.2244 | 0 | 0.033529 | Y | 53.3842 | 28.2357 | 47.11% | Y | 28.4047 | 54.6984 |  | 568094.5753 | 47.3412 | 820476.5042 | 68.373 | -21.0318 | Y |  |  | #REF!
Single | Double | Small | Hotel | PTAC | Electric |  | 100 | SingleDoubleSmallHotelPTACElectric100 | 0.45927 | 13.6042 | 0 | 0.033529 | Y | 61.7548 | 36.6062 | 40.72% | Y | 28.4047 | 54.6984 |  | 568094.5753 | 47.3412 | 820476.5042 | 68.373 | -21.0318 | Y |  |  | #REF!
Double | Single | Small | Hotel | PTAC | Electric |  | 33 | DoubleSingleSmallHotelPTACElectric33 | 0.23855 | 4.558 | 0 | 0.033529 | Y | 56.6258 | 31.4772 | 44.41% | Y | 26.5066 | 20.1219 |  | 530131.2676 | 44.1776 | 301829.1336 | 25.1524 | 19.0252 | Y |  |  | #REF!
Double | Single | Small | Hotel | PTAC | Electric |  | 100 | DoubleSingleSmallHotelPTACElectric100 | 0.23945 | 5.6987 | 0 | 0.033529 | Y | 61.9924 | 36.8439 | 40.57% | Y | 26.5066 | 20.1219 |  | 530131.2676 | 44.1776 | 301829.1336 | 25.1524 | 19.0252 | Y |  |  | 0.033529
Single | Single | Small | Hotel | PTHP | Electric | Low | 33 | SingleSingleSmallHotelPTHPElectricLow33 | 0.11905 | 6.0461 | 0 | 0.033529 | Y | 50.7112 | 25.5627 | 49.59% | Y | 28.4047 | 29.6018 |  | 568094.5753 | 47.3412 | 444027.4853 | 37.0023 | 10.3389 | Y |  |  | 0.033529
Single | Single | Small | Hotel | PTHP | Electric | High | 33 | SingleSingleSmallHotelPTHPElectricHigh33 | 47.5036 | 6.0461 | 0 | 0.033529 | Y | 50.7112 | 25.5627 | 49.59% | Y | 28.4047 | 29.6018 |  | 568094.5753 | 47.3412 | 444027.4853 | 37.0023 | 10.3389 | Y |  |  | 0.033529
Single | Single | Small | Hotel | PTHP | Electric | Low | 100 | SingleSingleSmallHotelPTHPElectricLow100 | 0.14734 | 7.2822 | 0 | 0.033529 | Y | 56.6865 | 31.538 | 44.36% | Y | 28.4047 | 29.6018 |  | 568094.5753 | 47.3412 | 444027.4853 | 37.0023 | 10.3389 | Y
Single | Single | Small | Hotel | PTHP | Electric | High | 100 | SingleSingleSmallHotelPTHPElectricHigh100 | 47.5333 | 7.2822 | 0 | 0.033529 | Y | 56.6865 | 31.538 | 44.36% | Y | 28.4047 | 29.6018 |  | 568094.5753 | 47.3412 | 444027.4853 | 37.0023 | 10.3389 | Y |  |  | 0.033529
Single | Double | Small | Hotel | PTHP | Electric | Low | 33 | SingleDoubleSmallHotelPTHPElectricLow33 | 0.15066 | 11.2244 | 0 | 0.033529 | Y | 50.7112 | 25.5627 | 49.59% | Y | 28.4047 | 54.6984 |  | 568094.5753 | 47.3412 | 820476.5042 | 68.373 | -21.0318 | Y |  |  | 0.033529
Single | Double | Small | Hotel | PTHP | Electric | High | 33 | SingleDoubleSmallHotelPTHPElectricHigh33 | 47.4252 | 11.2244 | 0 | 0.033529 | Y | 50.7112 | 25.5627 | 49.59% | Y | 28.4047 | 54.6984 |  | 568094.5753 | 47.3412 | 820476.5042 | 68.373 | -21.0318 | Y |  |  | 0.033529
Single | Double | Small | Hotel | PTHP | Electric | Low | 100 | SingleDoubleSmallHotelPTHPElectricLow100 | 0.19401 | 13.6042 | 0 | 0.033529 | Y | 56.6865 | 31.538 | 44.36% | Y | 28.4047 | 54.6984 |  | 568094.5753 | 47.3412 | 820476.5042 | 68.373 | -21.0318 | Y
Single | Double | Small | Hotel | PTHP | Electric | High | 100 | SingleDoubleSmallHotelPTHPElectricHigh100 | 47.8443 | 13.6042 | 0 | 0.033529 | Y | 56.6865 | 31.538 | 44.36% | Y | 28.4047 | 54.6984 |  | 568094.5753 | 47.3412 | 820476.5042 | 68.373 | -21.0318 | Y |  |  | 0.033529
Double | Single | Small | Hotel | PTHP | Electric | Low | 33 | DoubleSingleSmallHotelPTHPElectricLow33 | 0.10405 | 4.558 | 0 | 0.033529 | Y | 48.8359 | 23.6873 | 51.5% | Y | 26.5066 | 20.1219 |  | 530131.2676 | 44.1776 | 301829.1336 | 25.1524 | 19.0252 | Y |  |  | 0.033529
Double | Single | Small | Hotel | PTHP | Electric | High | 33 | DoubleSingleSmallHotelPTHPElectricHigh33 | 23.4641 | 4.558 | 0 | 0.033529 | Y | 48.8359 | 23.6873 | 51.5% | Y | 26.5066 | 20.1219 |  | 530131.2676 | 44.1776 | 301829.1336 | 25.1524 | 19.0252 | Y |  |  | 0.033529
Double | Single | Small | Hotel | PTHP | Electric | Low | 100 | DoubleSingleSmallHotelPTHPElectricLow100 | 0.099065 | 5.6987 | 0 | 0.033529 | Y | 55.8014 | 30.6528 | 45.07% | Y | 26.5066 | 20.1219 |  | 530131.2676 | 44.1776 | 301829.1336 | 25.1524 | 19.0252 | Y
Double | Single | Small | Hotel | PTHP | Electric | High | 100 | DoubleSingleSmallHotelPTHPElectricHigh100 | 21.9388 | 5.6987 | 0 | 0.033529 | Y | 55.8014 | 30.6528 | 45.07% | Y | 26.5066 | 20.1219 |  | 530131.2676 | 44.1776 | 301829.1336 | 25.1524 | 19.0252 | Y |  |  | 0.033529
Single | Single | Large | Hotel | FCU | Electric |  | 33 | SingleSingleLargeHotelFCUElectric33 | 0.065346 | 4.3186 | 0 |  | Y | 110.1377 | 84.9892 | 22.83% | Y | 37.0563 | 93.6999 |  | 741126.2429 | 61.7605 | 1405498.6823 | 117.1249 | -55.3644 | Y |  |  | #REF!
Single | Single | Large | Hotel | FCU | Electric |  | 100 | SingleSingleLargeHotelFCUElectric100 | 0.10877 | 5.2016 | 0 |  | Y | 116.4981 | 91.3495 | 21.59% | Y | 37.0563 | 93.6999 |  | 741126.2429 | 61.7605 | 1405498.6823 | 117.1249 | -55.3644 | Y |  |  | #REF!
Single | Double | Large | Hotel | FCU | Electric |  | 33 | SingleDoubleLargeHotelFCUElectric33 | 0.36073 | 8.0174 | 0 |  | Y | 110.1377 | 84.9892 | 22.83% | Y | 37.0563 | 186.7205 |  | 741126.2429 | 61.7605 | 2800807.0289 | 233.4006 | -171.6401 | Y |  |  | #REF!
Single | Double | Large | Hotel | FCU | Electric |  | 100 | SingleDoubleLargeHotelFCUElectric100 | 0.54053 | 9.7173 | 0 |  | Y | 116.4981 | 91.3495 | 21.59% | Y | 37.0563 | 186.7205 |  | 741126.2429 | 61.7605 | 2800807.0289 | 233.4006 | -171.6401 | Y |  |  | #REF!
Double | Single | Large | Hotel | FCU | Electric |  | 33 | DoubleSingleLargeHotelFCUElectric33 | 0.035928 | 3.2557 | 0 |  | Y | 103.0964 | 77.9479 | 24.39% | Y | 32.156 | 75.6363 |  | 643119.5558 | 53.5933 | 1134543.8976 | 94.5453 | -40.952 | Y |  |  | #REF!
Double | Single | Large | Hotel | FCU | Electric |  | 100 | DoubleSingleLargeHotelFCUElectric100 | 0.077719 | 4.0705 | 0 |  | Y | 109.3794 | 84.2308 | 22.99% | Y | 32.156 | 75.6363 |  | 643119.5558 | 53.5933 | 1134543.8976 | 94.5453 | -40.952 | Y |  |  | #REF!
Single | Single | Large | Hotel | FCU | Natural Gas |  | 33 | SingleSingleLargeHotelFCUNatural Gas33 | 0 | 4.3186 | 0.0038722 |  | Y | 111.2992 | 86.1506 | 22.6% | Y | 37.0563 | 93.6999 |  | 741126.2429 | 61.7605 | 1405498.6823 | 117.1249 | -55.3644 | Y |  |  | #REF!
Single | Single | Large | Hotel | FCU | Natural Gas |  | 100 | SingleSingleLargeHotelFCUNatural Gas100 | 0 | 5.2016 | 0.0048633 |  | Y | 117.6789 | 92.5304 | 21.37% | Y | 37.0563 | 93.6999 |  | 741126.2429 | 61.7605 | 1405498.6823 | 117.1249 | -55.3644 | Y |  |  | #REF!
Single | Double | Large | Hotel | FCU | Natural Gas |  | 33 | SingleDoubleLargeHotelFCUNatural Gas33 | 0 | 8.0174 | 0.0028885 |  | Y | 111.2992 | 86.1506 | 22.6% | Y | 37.0563 | 186.7205 |  | 741126.2429 | 61.7605 | 2800807.0289 | 233.4006 | -171.6401 | Y |  |  | #REF!
Single | Double | Large | Hotel | FCU | Natural Gas |  | 100 | SingleDoubleLargeHotelFCUNatural Gas100 | 0 | 9.7173 | 0.0036631 |  | Y | 117.6789 | 92.5304 | 21.37% | Y | 37.0563 | 186.7205 |  | 741126.2429 | 61.7605 | 2800807.0289 | 233.4006 | -171.6401 | Y |  |  | #REF!
Double | Single | Large | Hotel | FCU | Natural Gas |  | 33 | DoubleSingleLargeHotelFCUNatural Gas33 | 0 | 3.2557 | 0.0015323 |  | Y | 104.1237 | 78.9752 | 24.15% | Y | 32.156 | 75.6363 |  | 643119.5558 | 53.5933 | 1134543.8976 | 94.5453 | -40.952 | Y |  |  | #REF!
Double | Single | Large | Hotel | FCU | Natural Gas |  | 100 | DoubleSingleLargeHotelFCUNatural Gas100 | 0 | 4.0705 | 0.0033663 |  | Y | 110.7392 | 85.5906 | 22.71% | Y | 32.156 | 75.6363 |  | 643119.5558 | 53.5933 | 1134543.8976 | 94.5453 | -40.952 | Y |  |  | -1.5763
Single | Single |  | PS | FCU | Electric |  |  | SingleSinglePSFCUElectric | 11.4771 | 1.2037 | 0 |  | Y | 52.7062 | 44.4152 | 15.73% | Y | 29.217 | 26.9659 |  | 2337357.7564 | 194.7798 | 269659.1444 | 22.4716 | 172.3082 | Y |  |  | 0.68905
Single | Double |  | PS | FCU | Electric |  |  | SingleDoublePSFCUElectric | 10.5594 | 2.1225 | 0 |  | Y | 52.7062 | 44.4152 | 15.73% | Y | 29.0669 | 47.886 |  | 2325352.0325 | 193.7793 | 478859.7248 | 39.905 | 153.8744 | Y |  |  | 0.68905
Double | Single |  | PS | FCU | Electric |  |  | DoubleSinglePSFCUElectric | 5.9767 | 1.0194 | 0 |  | Y | 49.3542 | 41.0631 | 16.8% | Y | 26.3232 | 16.8093 |  | 2105853.1028 | 175.4878 | 168092.6109 | 14.0077 | 161.48 | Y |  |  | 0.68905
Single | Single |  | PS | VAV | Electric |  |  | SingleSinglePSVAVElectric | 15.218 | 5.0873 | 0 |  | Y | 59.4106 | 51.1196 | 13.96% | Y | 29.217 | 26.9659 |  | 2337357.7564 | 194.7798 | 269659.1444 | 22.4716 | 172.3082 | Y |  |  | 0.32199
Single | Double |  | PS | VAV | Electric |  |  | SingleDoublePSVAVElectric | 15.0914 | 8.1155 | 0 |  | Y | 59.4106 | 51.1196 | 13.96% | Y | 29.0669 | 47.886 |  | 2325352.0325 | 193.7793 | 478859.7248 | 39.905 | 153.8744 | Y |  |  | 0.32199
Double | Single |  | PS | VAV | Electric |  |  | DoubleSinglePSVAVElectric | 11.031 | 4.1236 | 0 |  | Y | 54.822 | 46.531 | 15.12% | Y | 26.3232 | 16.8093 |  | 2105853.1028 | 175.4878 | 168092.6109 | 14.0077 | 161.48 | Y |  |  | 0.32199
Single | Single |  | PS | FCU | Natural Gas |  |  | SingleSinglePSFCUNatural Gas | 0 | 1.2037 | 0.4895 |  | Y | 56.9136 | 48.6226 | 14.57% | Y | 29.217 | 26.9659 |  | 2337357.7564 | 194.7798 | 269659.1444 | 22.4716 | 172.3082 | Y |  |  | 0.68905
Single | Double |  | PS | FCU | Natural Gas |  |  | SingleDoublePSFCUNatural Gas | 0 | 2.1225 | 0.45036 |  | Y | 56.9136 | 48.6226 | 14.57% | Y | 29.0669 | 47.886 |  | 2325352.0325 | 193.7793 | 478859.7248 | 39.905 | 153.8744 | Y |  |  | 0.68905
Double | Single |  | PS | FCU | Natural Gas |  |  | DoubleSinglePSFCUNatural Gas | 0 | 1.0194 | 0.25491 |  | Y | 52.7246 | 44.4335 | 15.73% | Y | 26.3232 | 16.8093 |  | 2105853.1028 | 175.4878 | 168092.6109 | 14.0077 | 161.48 | Y |  |  | 0.68905
Single | Single |  | PS | VAV | Natural Gas |  |  | SingleSinglePSVAVNatural Gas | 0 | 5.0873 | 0.64905 |  | Y | 64.9834 | 56.6923 | 12.76% | Y | 29.217 | 26.9659 |  | 2337357.7564 | 194.7798 | 269659.1444 | 22.4716 | 172.3082 | Y |  |  | 0.32199
Single | Double |  | PS | VAV | Natural Gas |  |  | SingleDoublePSVAVNatural Gas | 0 | 8.1155 | 0.64365 |  | Y | 64.9834 | 56.6923 | 12.76% | Y | 29.0669 | 47.886 |  | 2325352.0325 | 193.7793 | 478859.7248 | 39.905 | 153.8744 | Y |  |  | 0.32199
Double | Single |  | PS | VAV | Natural Gas |  |  | DoubleSinglePSVAVNatural Gas | 0 | 4.1236 | 0.47047 |  | Y | 59.5943 | 51.3033 | 13.91% | Y | 26.3232 | 16.8093 |  | 2105853.1028 | 175.4878 | 168092.6109 | 14.0077 | 161.48 | Y |  |  | 0.32199
Single | Single |  | SS | FCU | Electric |  |  | SingleSingleSSFCUElectric | 12.4996 | 1.2874 | 0 |  | Y | 74.5873 | 66.2963 | 11.12% | Y | 19.157 | 24.776 |  | 1532558.1624 | 127.7132 | 247759.6031 | 20.6466 | 107.0665 | Y |  |  | 0.68905
Single | Double |  | SS | FCU | Electric |  |  | SingleDoubleSSFCUElectric | 11.5008 | 2.413 | 0 |  | Y | 74.5873 | 66.2963 | 11.12% | Y | 19.0129 | 45.7793 |  | 1521029.4674 | 126.7525 | 457792.7418 | 38.1494 | 88.6031 | Y |  |  | 0.68905
Double | Single |  | SS | FCU | Electric |  |  | DoubleSingleSSFCUElectric | 6.4473 | 1.0904 | 0 |  | Y | 70.2601 | 61.9691 | 11.8% | Y | 17.2576 | 15.6764 |  | 1380606.1653 | 115.0505 | 156764.1147 | 13.0637 | 101.9868 | Y |  |  | 0.68905
Single | Single |  | SS | VAV | Electric |  |  | SingleSingleSSVAVElectric | 16.9528 | 5.3603 | 0 |  | Y | 78.3585 | 70.0674 | 10.58% | Y | 19.157 | 24.776 |  | 1532558.1624 | 127.7132 | 247759.6031 | 20.6466 | 107.0665 | Y |  |  | 0.32199
Single | Double |  | SS | VAV | Electric |  |  | SingleDoubleSSVAVElectric | 15.6129 | 9.1059 | 0 |  | Y | 78.3585 | 70.0674 | 10.58% | Y | 19.0129 | 45.7793 |  | 1521029.4674 | 126.7525 | 457792.7418 | 38.1494 | 88.6031 | Y |  |  | 0.32199
Double | Single |  | SS | VAV | Electric |  |  | DoubleSingleSSVAVElectric | 12.0936 | 4.3339 | 0 |  | Y | 73.7863 | 65.4952 | 11.24% | Y | 17.2576 | 15.6764 |  | 1380606.1653 | 115.0505 | 156764.1147 | 13.0637 | 101.9868 | Y |  |  | 0.32199
Single | Single |  | SS | FCU | Natural Gas |  |  | SingleSingleSSFCUNatural Gas | 0 | 1.2874 | 0.53311 |  | Y | 82.1113 | 73.8202 | 10.1% | Y | 19.157 | 24.776 |  | 1532558.1624 | 127.7132 | 247759.6031 | 20.6466 | 107.0665 | Y |  |  | 0.68905
Single | Double |  | SS | FCU | Natural Gas |  |  | SingleDoubleSSFCUNatural Gas | 0 | 2.413 | 0.49051 |  | Y | 82.1113 | 73.8202 | 10.1% | Y | 19.0129 | 45.7793 |  | 1521029.4674 | 126.7525 | 457792.7418 | 38.1494 | 88.6031 | Y |  |  | 0.68905
Double | Single |  | SS | FCU | Natural Gas |  |  | DoubleSingleSSFCUNatural Gas | 0 | 1.0904 | 0.27498 |  | Y | 77.0938 | 68.8028 | 10.75% | Y | 17.2576 | 15.6764 |  | 1380606.1653 | 115.0505 | 156764.1147 | 13.0637 | 101.9868 | Y |  |  | 0.68905
Single | Single |  | SS | VAV | Natural Gas |  |  | SingleSingleSSVAVNatural Gas | 0 | 5.3603 | 0.72304 |  | Y | 87.1139 | 78.8229 | 9.517% | Y | 19.157 | 24.776 |  | 1532558.1624 | 127.7132 | 247759.6031 | 20.6466 | 107.0665 | Y |  |  | 0.32199
Single | Double |  | SS | VAV | Natural Gas |  |  | SingleDoubleSSVAVNatural Gas | 0 | 9.1059 | 0.66589 |  | Y | 87.1139 | 78.8229 | 9.517% | Y | 19.0129 | 45.7793 |  | 1521029.4674 | 126.7525 | 457792.7418 | 38.1494 | 88.6031 | Y |  |  | 0.32199
Double | Single |  | SS | VAV | Natural Gas |  |  | DoubleSingleSSVAVNatural Gas | 0 | 4.3339 | 0.51537 |  | Y | 82.2746 | 73.9836 | 10.08% | Y | 17.2576 | 15.6764 |  | 1380606.1653 | 115.0505 | 156764.1147 | 13.0637 | 101.9868 | Y |  |  | 0.32199
Single | Single |  | Hosp | VAV | Electric |  |  | SingleSingleHospVAVElectric | 28.8332 | 12.3824 | 0 |  | Y | 204.4148 | 192.7624 | 5.7% | Y | 20.8647 | 14.063 |  | 4381577.776 | 365.1315 | 168756.2748 | 14.063 | 351.0685 | Y |  |  | 0.57542
Single | Double |  | Hosp | VAV | Electric |  |  | SingleDoubleHospVAVElectric | 34.0114 | 15.7058 | 0 |  | Y | 204.4148 | 192.7624 | 5.7% | Y | 20.8647 | 24.2892 |  | 4381577.776 | 365.1315 | 291470.6327 | 24.2892 | 340.8423 | Y |  |  | 0.57542
Double | Single |  | Hosp | VAV | Electric |  |  | DoubleSingleHospVAVElectric | 17.0499 | 6.9358 | 0 |  | Y | 204.4148 | 192.7624 | 5.7% | Y | 22.101 | 8.2079 |  | 4641216.1172 | 386.768 | 98494.6427 | 8.2079 | 378.5601 | Y |  |  | 0.57542
Single | Single |  | Hosp | VAV | Natural Gas |  |  | SingleSingleHospVAVNatural Gas | 0 | 12.3824 | 1.2603 |  | Y | 230.1992 | 218.5468 | 5.062% | Y | 20.8647 | 14.063 |  | 4381577.776 | 365.1315 | 168756.2748 | 14.063 | 351.0685 | Y |  |  | 0.57542
Single | Double |  | Hosp | VAV | Natural Gas |  |  | SingleDoubleHospVAVNatural Gas | 0 | 15.7058 | 1.5031 |  | Y | 230.1992 | 218.5468 | 5.062% | Y | 20.8647 | 24.2892 |  | 4381577.776 | 365.1315 | 291470.6327 | 24.2892 | 340.8423 | Y |  |  | 0.57542
Double | Single |  | Hosp | VAV | Natural Gas |  |  | DoubleSingleHospVAVNatural Gas | 0 | 6.9358 | 0.73653 |  | Y | 230.1992 | 218.5468 | 5.062% | Y | 22.101 | 8.2079 |  | 4641216.1172 | 386.768 | 98494.6427 | 8.2079 | 378.5601 | Y |  |  | 0.57542
Single | Single | Low | MF | PTAC | Electric |  |  | SingleSingleLowMFPTACElectric | 9.3268 | 5.4637 | 0 |  | Y | 44.472 | 39.6112 | 10.93% | Y | 16.9578 | 31.7117 |  | 1526200.8628 | 127.1834 | 317116.7111 | 26.4264 | 100.757 | Y | 0.80802 | 0.918 | 0.28907
Single | Double | Low | MF | PTAC | Electric |  |  | SingleDoubleLowMFPTACElectric | 6.8175 | 10.2374 | 0 |  | Y | 45.6137 | 40.7529 | 10.66% | Y | 16.9578 | 58.5049 |  | 1526200.8628 | 127.1834 | 585048.5029 | 48.754 | 78.4294 | Y | 0.80802 | 0.918 | 0.28907
Double | Single | Low | MF | PTAC | Electric |  |  | DoubleSingleLowMFPTACElectric | 4.2241 | 3.9652 | 0 |  | Y | 42.4892 | 37.6283 | 11.44% | Y | 14.0724 | 21.5897 |  | 1266517.0199 | 105.5431 | 215896.9862 | 17.9914 | 87.5517 | Y | 0.80802 | 0.918 | 0.28907
Single | Single | Mid | MF | FCU | Electric |  |  | SingleSingleMidMFFCUElectric | 8.095 | 4.7229 | 0 |  | Y | 42.1565 | 37.2956 | 11.53% | Y | 14.1333 | 24.1347 |  | 1272000.9549 | 106.0001 | 241347.458 | 20.1123 | 85.8878 | Y | 0.80802 | 0.918 | 0.55233
Single | Double | Mid | MF | FCU | Electric |  |  | SingleDoubleMidMFFCUElectric | 5.883 | 9.4893 | 0 |  | Y | 42.1565 | 37.2956 | 11.53% | Y | 14.1333 | 46.3741 |  | 1272000.9549 | 106.0001 | 463741.1679 | 38.6451 | 67.355 | Y | 0.80802 | 0.918 | 0.55233
Double | Single | Mid | MF | FCU | Electric |  |  | DoubleSingleMidMFFCUElectric | 3.196 | 3.412 | 0 |  | Y | 39.3661 | 34.5053 | 12.35% | Y | 11.838 | 10.5346 |  | 1065420.7746 | 88.7851 | 105346.132 | 8.7788 | 80.0062 | Y | 0.80802 | 0.918 | 0.55233
Single | Single | Mid | MF | FCU | Natural Gas |  |  | SingleSingleMidMFFCUNatural Gas | 0 | 4.7229 | 0.34525 |  | Y | 44.492 | 39.6312 | 10.93% | Y | 14.1333 | 24.1347 |  | 1272000.9549 | 106.0001 | 241347.458 | 20.1123 | 85.8878 | Y | 0.80802 | 0.918 | 0.55233
Single | Double | Mid | MF | FCU | Natural Gas |  |  | SingleDoubleMidMFFCUNatural Gas | 0 | 9.4893 | 0.25091 |  | Y | 44.492 | 39.6312 | 10.93% | Y | 14.1333 | 46.3741 |  | 1272000.9549 | 106.0001 | 463741.1679 | 38.6451 | 67.355 | Y | 0.80802 | 0.918 | 0.55233
Double | Single | Mid | MF | FCU | Natural Gas |  |  | DoubleSingleMidMFFCUNatural Gas | 0 | 3.412 | 0.13631 |  | Y | 41.0992 | 36.2384 | 11.83% | Y | 11.838 | 10.5346 |  | 1065420.7746 | 88.7851 | 105346.132 | 8.7788 | 80.0062 | Y | 0.80802 | 0.918 | 0.55233
0
0

## Regresson List_Office
Energy Savings Regressions | [6 empty] | Regression Form (a+bx+cx^2)
[7 empty] | Heating Coefficients |  |  | Cooling Coefficients |  |  | Notes/Assumptions | Heating Savings Curve Comparisons
No. | Base | SGS Type | Office Size | HVAC/Fuel Type | Fuel Type | Hours | a | b | c | a | b | c |  | HDD | 1 v 10 |  | % delta
1 | Single | Single | Mid | PVAV_Elec | Electric | 2080 | 0.87047 | 0.001676 | -5.82e-08 | 2.4043 | 0.00056251 | -9.7e-09 |  | 0 | 0.87047 | 1.0451 | -20.06%
2 | Single | Single | Mid | PVAV_Elec | Electric | 2912 | 1.695 | 0.0023052 | -8.55e-08 | 3.7648 | 0.0011532 | -6.65e-08 |  | 1000 | 2.4883 | 2.7875 | -12.03%
3 | Single | Single | Mid | PVAV_Elec | Electric | 8760 | 16.0041 | 0.0025681 | -6.39e-08 | 6.1823 | 0.0040024 | -2.414e-07 |  | 2000 | 3.9896 | 4.4055 | -10.42%
4 | Single | Double | Mid | PVAV_Elec | Electric | 2080 | 1.2309 | 0.0012507 | -9.1e-09 | 4.2025 | 0.0010761 | -7.28e-08 |  | 3000 | 5.3746 | 5.8993 | -9.761%
5 | Single | Double | Mid | PVAV_Elec | Electric | 2912 | 1.9904 | 0.0018291 | -2.58e-08 | 5.4563 | 0.0024885 | -2.236e-07 |  | 4000 | 6.6432 | 7.2686 | -9.414%
6 | Single | Double | Mid | PVAV_Elec | Electric | 8760 | 19.7294 | 0.0019487 | -3.6e-08 | 7.4924 | 0.0055275 | -3.6e-07 |  | 5000 | 7.7954 | 8.5136 | -9.214%
7 | Double | Single | Mid | PVAV_Elec | Electric | 2080 | 0.36809 | 0.00078224 | -2.94e-08 | 1.2341 | 0.00086291 | -8.2844e-08 |  | 6000 | 8.8312 | 9.6343 | -9.094%
8 | Double | Single | Mid | PVAV_Elec | Electric | 2912 | 0.90209 | 0.00085224 | -1.84e-08 | 1.2423 | 0.0018367 | -1.7058e-07 |  | 7000 | 9.7506 | 10.6306 | -9.026%
9 | Double | Single | Mid | PVAV_Elec | Electric | 8760 | 10.3089 | 0.00060965 | -6.3e-09 | 1.6695 | 0.0033281 | -2.268e-07 |  | 8000 | 10.5536 | 11.5026 | -8.992%
10 | Single | Single | Large | VAV | Electric | 2080 | 1.0451 | 0.0018046 | -6.2176e-08 | 2.9952 | 0.00054436 | -1.1922e-08 |  | 9000 | 11.2401 | 12.2502 | -8.986%
11 | Single | Single | Large | VAV | Electric | 2912 | 1.9632 | 0.00248 | -8.4257e-08 | 4.691 | 0.0011371 | -6.8371e-08 |  | 10000 | 11.8103 | 12.8734 | -9.001%
12 | Single | Single | Large | VAV | Electric | 8760 | 17.8817 | 0.0027347 | -6.9507e-08 | 7.8631 | 0.0041845 | -2.5866e-07 |  | 11000 | 12.2641 | 13.3723 | -9.036%
13 | Single | Double | Large | VAV | Electric | 2080 | 1.4248 | 0.0013539 | -1.0265e-08 | 5.1829 | 0.0010799 | -8.2357e-08 |  | 12000 | 12.6015 | 13.7469 | -9.089%
14 | Single | Double | Large | VAV | Electric | 2912 | 2.3366 | 0.0019452 | -2.5309e-08 | 6.795 | 0.0025987 | -2.4798e-07
15 | Single | Double | Large | VAV | Electric | 8760 | 22.0222 | 0.0020809 | -4.0988e-08 | 9.5019 | 0.0059375 | -4.1904e-07 |  | HDD | 2 v 11 |  | % delta
16 | Double | Single | Large | VAV | Electric | 2080 | 0.4342 | 0.00085233 | -3.2055e-08 | 1.5494 | 0.00091568 | -9.2914e-08 |  | 0 | 1.695 | 1.9632 | -15.83%
17 | Double | Single | Large | VAV | Electric | 2912 | 1.0306 | 0.00093112 | -2.0723e-08 | 1.5594 | 0.0020586 | -2.0486e-07 |  | 1000 | 3.9147 | 4.3589 | -11.35%
18 | Double | Single | Large | VAV | Electric | 8760 | 11.4976 | 0.00062221 | -5.8971e-09 | 2.2115 | 0.0036711 | -2.6307e-07 |  | 2000 | 5.9633 | 6.5862 | -10.44%
19 | Single | Single | Mid | PVAV_Gas | Natural Gas | 2080 | 0.042695 | 8.1867e-05 | -2.8552e-09 | 2.4043 | 0.00056251 | -9.7e-09 |  | 3000 | 7.841 | 8.6449 | -10.25%
20 | Single | Single | Mid | PVAV_Gas | Natural Gas | 2912 | 0.083713 | 0.00011194 | -4.1327e-09 | 3.7648 | 0.0011532 | -6.65e-08 |  | 4000 | 9.5477 | 10.5351 | -10.34%
21 | Single | Single | Mid | PVAV_Gas | Natural Gas | 8760 | 0.78714 | 0.00012298 | -1.782e-07 | 6.1823 | 0.0040024 | -2.414e-07 |  | 5000 | 11.0834 | 12.2567 | -10.59%
22 | Single | Double | Mid | PVAV_Gas | Natural Gas | 2080 | 0.058867 | 6.1357e-05 | -4.908e-10 | 4.2025 | 0.0010761 | -7.28e-08 |  | 6000 | 12.448 | 13.8099 | -10.94%
23 | Single | Double | Mid | PVAV_Gas | Natural Gas | 2912 | 0.096359 | 8.942e-05 | -1.2781e-09 | 5.4563 | 0.0024885 | -2.236e-07 |  | 7000 | 13.6417 | 15.1946 | -11.38%
24 | Single | Double | Mid | PVAV_Gas | Natural Gas | 8760 | 0.95972 | 9.5436e-05 | -1.8077e-09 | 7.4924 | 0.0055275 | -3.6e-07 |  | 8000 | 14.6644 | 16.4107 | -11.91%
25 | Double | Single | Mid | PVAV_Gas | Natural Gas | 2080 | 0.017465 | 3.824e-05 | -1.454e-09 | 1.2341 | 0.00086291 | -8.2844e-08 |  | 9000 | 15.5161 | 17.4583 | -12.52%
26 | Double | Single | Mid | PVAV_Gas | Natural Gas | 2912 | 0.043295 | 4.1592e-05 | -9.041e-10 | 1.2423 | 0.0018367 | -1.7058e-07 |  | 10000 | 16.1967 | 18.3374 | -13.22%
27 | Double | Single | Mid | PVAV_Gas | Natural Gas | 8760 | 0.50115 | 2.9516e-05 | -2.97e-10 | 1.6695 | 0.0033281 | -2.268e-07 |  | 11000 | 16.7064 | 19.048 | -14.02%
28 | Single | Single | Large | VAV | Natural Gas | 2080 | 0.051034 | 8.7885e-05 | -3.0213e-09 | 2.9952 | 0.00054436 | -1.1922e-08 |  | 12000 | 17.0451 | 19.5901 | -14.93%
29 | Single | Single | Large | VAV | Natural Gas | 2912 | 0.09622 | 0.00012082 | -4.1033e-09 | 4.691 | 0.0011371 | -6.8371e-08
30 | Single | Single | Large | VAV | Natural Gas | 8760 | 0.87218 | 0.00013319 | -3.3867e-09 | 7.8631 | 0.0041845 | -2.5866e-07 |  | HDD | 3 v 12 |  | % delta
31 | Single | Double | Large | VAV | Natural Gas | 2080 | 0.068584 | 6.5753e-05 | -4.825e-10 | 5.1829 | 0.0010799 | -8.2357e-08 |  | 0 | 16.0041 | 17.8817 | -11.73%
32 | Single | Double | Large | VAV | Natural Gas | 2912 | 0.11084 | 9.4884e-05 | -1.2252e-09 | 6.795 | 0.0025987 | -2.4798e-07 |  | 1000 | 18.5083 | 20.5469 | -11.01%
33 | Single | Double | Large | VAV | Natural Gas | 8760 | 1.0746 | 0.00010117 | -2.0052e-09 | 9.5019 | 0.0059375 | -4.1904e-07 |  | 2000 | 20.8848 | 23.0731 | -10.48%
34 | Double | Single | Large | VAV | Natural Gas | 2080 | 0.021081 | 4.1282e-05 | -1.5477e-09 | 1.5494 | 0.00091568 | -9.2914e-08 |  | 3000 | 23.1334 | 25.4603 | -10.06%
35 | Double | Single | Large | VAV | Natural Gas | 2912 | 0.049487 | 4.5563e-05 | -1.0305e-09 | 1.5594 | 0.0020586 | -2.0486e-07 |  | 4000 | 25.2543 | 27.7085 | -9.718%
36 | Double | Single | Large | VAV | Natural Gas | 8760 | 0.5567 | 3.1069e-05 | -3.498e-10 | 2.2115 | 0.0036711 | -2.6307e-07 |  | 5000 | 27.2473 | 29.8176 | -9.433%
[14 empty] | 6000 | 29.1125 | 31.7878 | -9.189%
Peak Load Reduction Regressions | [6 empty] | Regression Form (a+bx+cx^2) | [6 empty] | 7000 | 30.85 | 33.6189 | -8.975%
[7 empty] | Baseline Cooling Load Coefficients |  |  | Cooling Coefficients |  |  |  | 8000 | 32.4596 | 35.311 | -8.784%
No. | Base | SGS Type | Office Size | HVAC System Type | Location |  | a | b | c | a | b | c |  | 9000 | 33.9415 | 36.8641 | -8.611%
1 | Single | Single | Mid |  |  |  | 19.7937 | 0.0034283 | -3.153e-07 | 21.1474 | 0.0060445 | -5.603e-07 |  | 10000 | 35.2955 | 38.2782 | -8.451%
2 | Single | Double | Mid |  |  |  | 19.7937 | 0.0034283 | -3.153e-07 | 45.4062 | 0.0096502 | -8.115e-07 |  | 11000 | 36.5218 | 39.5533 | -8.301%
3 | Double | Single | Mid |  |  |  | 17.8041 | 0.0027898 | -2.34e-07 | 15.6944 | 0.0034111 | -2.989e-07 |  | 12000 | 37.6202 | 40.6894 | -8.158%
4 | Single | Single | Large |  |  |  | 24.3073 | 0.0023954 | -2.005e-07 | 19.9673 | 0.0070543 | -7.612e-07
5 | Single | Double | Large |  |  |  | 24.3073 | 0.0023954 | -2.005e-07 | 46.0266 | 0.011787 | -1.1328e-06
6 | Double | Single | Large |  |  |  | 23.0197 | 0.0015842 | -7.35e-08 | 16.6364 | 0.0047085 | -5.485e-07
Baseline EUI Regressions | [6 empty] | Regression Form (a+bx+cx^2)
Coefficients
No. | Base | CSW Type | Office Size | Fuel | Location | Hours | a | b | c
1 | Single | N/A | Mid | Electric | N/A | 2080 | 55.1811 | -0.002839 | 4.1e-07
2 | Single | N/A | Mid | Electric | N/A | 2912 | 69.3419 | -0.0051025 | 6.6e-07
3 | Single | N/A | Mid | Electric | N/A | 8760 | 155.2883 | -0.012402 | 1.42e-06
4 | Double | N/A | Mid | Electric | N/A | 2080 | 56.4687 | -0.0036288 | 3.8e-07
5 | Double | N/A | Mid | Electric | N/A | 2912 | 66.1222 | -0.0050973 | 6e-07
6 | Double | N/A | Mid | Electric | N/A | 8760 | 132.8104 | -0.007426 | 8.1e-07
7 | Single | N/A | Mid | Gas | N/A | 2080 | 59.3124 | -0.00244 | 4.1e-07
8 | Single | N/A | Mid | Gas | N/A | 2912 | 74.8824 | -0.0048032 | 1.115e-06
9 | Single | N/A | Mid | Gas | N/A | 8760 | 163.5203 | -0.0062067 | 9.8e-07
10 | Double | N/A | Mid | Gas | N/A | 2080 | 59.7013 | -0.0047265 | 4.7e-07
11 | Double | N/A | Mid | Gas | N/A | 2912 | 70.9425 | -0.0063586 | 6.5e-07
12 | Double | N/A | Mid | Gas | N/A | 8760 | 139.89 | -0.010483 | 1.14e-06
13 | Single | N/A | Large | Electric | N/A | 2080 | 58.2415 | -0.00473 | 7.1e-07
14 | Single | N/A | Large | Electric | N/A | 2912 | 90.2995 | -0.0075784 | 1.08e-06
15 | Single | N/A | Large | Electric | N/A | 8760 | 151.3971 | -0.0088017 | 1.21e-06
16 | Double | N/A | Large | Electric | N/A | 2080 | 59.5296 | 0.0058856 | 7.8e-07
17 | Double | N/A | Large | Electric | N/A | 2912 | 88.8428 | -0.0088189 | 1.16e-06
18 | Double | N/A | Large | Electric | N/A | 8760 | 143.1419 | -0.0096109 | 1.16e-06
19 | Single | N/A | Large | Gas | N/A | 2080 | 59.4612 | -0.0041882 | 6e-07
20 | Single | N/A | Large | Gas | N/A | 2912 | 93.5545 | -0.0066678 | 1.02e-06
21 | Single | N/A | Large | Gas | N/A | 8760 | 154.7148 | -0.0065439 | 1.04e-06
22 | Double | N/A | Large | Gas | N/A | 2080 | 61.096 | -0.0049 | 6.7e-07
23 | Double | N/A | Large | Gas | N/A | 2912 | 90.4449 | -0.0066078 | 9.2e-07
24 | Double | N/A | Large | Gas | N/A | 8760 | 151.3476 | -0.010117 | 1.22e-06
Cooling Adjustment Regressoins Regressions | [6 empty] | a | b | c | d
Mid-size Office | [6 empty] | 0.69722 | -0.00010782 | 3.6051e-08 | -6.4e-12
Large Office | [6 empty] | 0.7793 | 4.963e-05 | -2.8839e-08 | 1e-12

## Regresson List_SH
Energy Savings Regressions | [6 empty] | Regression Form (a+bx+cx^2)
[7 empty] | Heating Coefficients |  |  | Cooling Coefficients |  |  | Heating Coefficients (Part 2)
No. | Base | CSW Type | Hotel Size | HVAC/Fuel Type | Fuel Type | Occupancy | a | b | c | a | b | c
1 | Single | Single | Small | PTAC | Electric | 33 | 0.26195 | 0.0011672 | 7.07e-08 | 1.0416 | 0.0014359 | -7.425e-08
2 | Single | Single | Small | PTAC | Electric | 100 | 0.34628 | 0.0017406 | 3.3033e-08 | 1.9828 | 0.0013242 | -3.5574e-08
3 | Single | Double | Small | PTAC | Electric | 33 | 0.33832 | 0.00093325 | 8.5301e-08 | 2.4891 | 0.0025642 | -1.423e-07
4 | Single | Double | Small | PTAC | Electric | 100 | 0.45927 | 0.0014362 | 5.3247e-08 | 3.861 | 0.0026635 | -1.156e-07
5 | Double | Single | Small | PTAC | Electric | 33 | 0.23855 | 0.00024276 | 5.61e-08 | 0.77436 | 0.0011276 | -6.5352e-08
6 | Double | Single | Small | PTAC | Electric | 100 | 0.23945 | 0.00080163 | 1.4955e-08 | 0.96197 | 0.0013188 | -6.1448e-08
7 | Single | Single | Small | PTHP | Electric | 33 | 0.11905 | 0.00042364 | 4.7421e-08 | 1.0416 | 0.0014359 | -7.425e-08 | 47.5036 | -0.011031 | 7.4216e-07
8 | Single | Single | Small | PTHP | Electric | 100 | 0.14734 | 0.00065798 | 3.4171e-08 | 1.9828 | 0.0013242 | -3.5574e-08 | 47.5333 | -0.010875 | 7.3864e-07
9 | Single | Double | Small | PTHP | Electric | 33 | 0.15066 | 0.00032914 | 5.2461e-08 | 2.4891 | 0.0025642 | -1.423e-07 | 47.4252 | -0.011071 | 7.4204e-07
10 | Single | Double | Small | PTHP | Electric | 100 | 0.19401 | 0.0005347 | 4.1346e-08 | 3.861 | 0.0026635 | -1.156e-07 | 47.8443 | -0.011024 | 7.4493e-07
11 | Double | Single | Small | PTHP | Electric | 33 | 0.10405 | 7.4317e-05 | 3.079e-08 | 0.77436 | 0.0011276 | -6.5352e-08 | 23.4641 | -0.0055318 | 3.6817e-07
12 | Double | Single | Small | PTHP | Electric | 100 | 0.099065 | 0.00030373 | 1.5623e-08 | 0.96197 | 0.0013188 | -6.1448e-08 | 21.9388 | -0.0050138 | 3.4055e-07
Peak Load Reduction Regressions | [6 empty] | Regression Form (a+bx+cx^2)
[7 empty] | Base Peak Load Coefficient |  |  | Cooling Reduction Coefficients
No. | Base | SGS Type | Hotel Size | HVAC System Type | Location |  | a | b | c | a | b | c
1 | Single | Single | Small | N/A | N/A |  | 16.4825 | 0.0040935 | -3.244e-07 | 13.683 | 0.0061771 | -5.891e-07
2 | Single | Double | Small | N/A | N/A |  | 16.4825 | 0.0040935 | -3.244e-07 | 24.7902 | 0.011711 | -1.1299e-06
3 | Double | Single | Small | N/A | N/A |  | 16.2543 | 0.0040813 | -4.02e-07 | 8.6455 | 0.0043684 | -4.061e-07
EUI Regressions | [6 empty] | Regression Form (a+bx+cx^2)
Coefficients
No. | Base | CSW Type | Hotel Size | HVAC/Fuel Type | Location | Occupancy | a | b | c
1 | Single | N/A | Small | PTAC | N/A | 33 | 53.3842 | -0.0018385 | 5.912e-07
3 | Single | N/A | Small | PTAC | N/A | 100 | 61.7548 | -0.0028943 | 6.6e-07
4 | Double | N/A | Small | PTAC | N/A | 33 | 56.6258 | -0.0021877 | 5.948e-07
6 | Double | N/A | Small | PTAC | N/A | 100 | 61.9924 | -0.0031041 | 6.701e-07
7 | Single | N/A | Small | PTHP | N/A | 33 | 50.7112 | -0.0053321 | 7.588e-07
9 | Single | N/A | Small | PTHP | N/A | 100 | 56.6865 | -0.0055582 | 7.785e-07
10 | Double | N/A | Small | PTHP | N/A | 33 | 48.8359 | -0.0046747 | 6.767e-07
12 | Double | N/A | Small | PTHP | N/A | 100 | 55.8014 | -0.0047838 | 6.515e-07
Cooling / Aux Split Regression |  |  | a | b | c | d
|  |  | 0.46864 | -0.00036016 | 1.0366e-07 | -1e-11

## Regresson List_LH
Energy Savings Regressions | [6 empty] | Regression Form (a+bx+cx^2) except PTHP which is Exponential Curve
[7 empty] | Heating Coefficients |  |  | Cooling Coefficients |  |  | Notes/Assumptions
No. | Base | CSW Type | Hotel Size | HVAC/Fuel Type | Fuel Type | Occupancy | a | b | c | a | b | c
1 | Single | Single | Large |  | Electric | 33 | 0.065346 | 0.0010554 | 3.98e-08 | 0.74399 | 0.0010256 | -5.3036e-08
2 | Single | Single | Large |  | Electric | 100 | 0.10877 | 0.0016539 | 1.17e-08 | 1.4163 | 0.00094583 | -2.541e-08
3 | Single | Double | Large |  | Electric | 33 | 0.36073 | 0.00037113 | 9.16e-08 | 1.7779 | 0.0018316 | -1.0164e-07
4 | Single | Double | Large |  | Electric | 100 | 0.54053 | 0.0011271 | -8.46e-08 | 2.7579 | 0.0019025 | -8.2571e-08
5 | Double | Single | Large |  | Electric | 33 | 0.035928 | 0.00032251 | 2.38e-08 | 0.55312 | 0.00080546 | -4.668e-08
6 | Double | Single | Large |  | Electric | 100 | 0.077719 | 0.00051203 | 1.76e-08 | 0.68712 | 0.000942 | -4.3891e-08
7 | Single | Single | Large |  | Gas | 33 | 0.0038722 | 4.4682e-05 | 1.719e-09 | 0.74399 | 0.0010256 | -5.3036e-08
8 | Single | Single | Large |  | Gas | 100 | 0.0048633 | 7.0633e-05 | 4.82e-10 | 1.4163 | 0.00094583 | -2.541e-08
9 | Single | Double | Large |  | Gas | 33 | 0.0028885 | 1.7714e-05 | 3.57e-09 | 1.7779 | 0.0018316 | -1.0164e-07
10 | Single | Double | Large |  | Gas | 100 | 0.0036631 | 3.5852e-05 | 3.2519e-09 | 2.7579 | 0.0019025 | -8.2571e-08
11 | Double | Single | Large |  | Gas | 33 | 0.0015323 | 1.3755e-05 | 1.0151e-09 | 0.55312 | 0.00080546 | -4.668e-08
12 | Double | Single | Large |  | Gas | 100 | 0.0033663 | 2.1778e-05 | 7.593e-10 | 0.68712 | 0.000942 | -4.3891e-08
Peak Load Reduction Regressions | [6 empty] | Regression Form (a+bx+cx^2)
[7 empty] | Base Peak Load Coefficient |  |  | Cooling Reduction Coefficients
No. | Base | SGS Type | Hotel Size | HVAC System Type | Location |  | a | b | c | a | b | c
1 | Single | Single | Large | N/A | N/A |  | 22.9423 | 0.0049987 | -4.175e-07 | 51.0672 | 0.016653 | -1.6018e-06
2 | Single | Double | Large | N/A | N/A |  | 22.9423 | 0.0049987 | -4.175e-07 | 111.6874 | 0.029645 | -2.8927e-06
3 | Double | Single | Large |  |  |  | 21.1662 | 0.0033299 | -2.018e-07 | 44.687 | 0.011554 | -1.0455e-06
Baseline EUI Regressions | [6 empty] | Regression Form (a+bx+cx^2)
Coefficients
No. | Base | CSW Type | Hotel Size | Fuel Type | Location | Occ | a | b | c
1 | Single | N/A | Large | Electric | N/A | 33 | 110.1377 | -0.0078283 | 9.88e-07
3 | Single | N/A | Large | Electric | N/A | 100 | 116.4981 | -0.0084816 | 1.0438e-06
4 | Double | N/A | Large | Electric | N/A | 33 | 103.0964 | -0.007085 | 8.928e-07
6 | Double | N/A | Large | Electric | N/A | 100 | 109.3794 | -0.0075483 | 9.197e-07
7 | Single | N/A | Large | Gas | N/A | 33 | 111.2992 | -0.0071869 | 1.0628e-06
9 | Single | N/A | Large | Gas | N/A | 100 | 117.6789 | -0.0078209 | 1.1174e-06
10 | Double | N/A | Large | Gas | N/A | 33 | 104.1237 | -0.0065781 | 9.638e-07
12 | Double | N/A | Large | Gas | N/A | 100 | 110.7392 | -0.0074406 | 1.0281e-06
Cooling / Aux Split Regression |  |  | a | b | c | d
|  |  | 0.62037 | -0.0001621 | -5.1812e-08 | -4e-12

## Regresson List_PS
Energy Savings Regressions | [5 empty] | Regression Form (a+bx+cx^2)
[6 empty] | Heating Coefficients |  |  | Cooling Coefficients |  |  | Notes/Assumptions (change from red to black when coefficients are dialed in)
No. | Base | CSW Type |  | HVAC Type | Fuel | a | b | c | a | b | c
1 | Single | Single |  | FCU | Elec | 0.053961 | 0.0021448 | -1.7946e-09 | 0.95809 | 0.00022102 | -1.2262e-09
2 | Single | Double |  | FCU | Elec | 0.13779 | 0.0019761 | -5.2529e-09 | 1.3489 | 0.00071388 | -1.9599e-08
3 | Double | Single |  | FCU | Elec | 0.0037853 | 0.0010767 | 7.4261e-09 | 0.81031 | 0.00018948 | -2.1621e-09
4 | Single | Single |  | VAV | Elec | 0.28479 | 0.0029384 | -2.75e-08 | 3.6664 | 0.0013575 | -7.74e-08
5 | Single | Double |  | VAV | Elec | 0.15624 | 0.0029248 | -2.49e-08 | 5.4819 | 0.0025477 | -1.718e-07
6 | Double | Single |  | VAV | Elec | 0.60465 | 0.0020275 | -1.47e-08 | 3.0243 | 0.001035 | -4.63e-08
7 | Single | Single |  | FCU | Gas | 0.0023014 | 9.1475e-05 | -7.65e-11 | 0.95809 | 0.00022102 | -1.2262e-09
8 | Single | Double |  | FCU | Gas | 0.0058768 | 8.4279e-05 | -2.24e-10 | 1.3489 | 0.00071388 | -1.9599e-08
9 | Double | Single |  | FCU | Gas | 0.00016144 | 4.5922e-05 | 3.167e-10 | 0.81031 | 0.00018948 | -2.1621e-09
10 | Single | Single |  | VAV | Gas | 0.012146 | 0.00012532 | -1.1729e-09 | 3.6664 | 0.0013575 | -7.74e-08
11 | Single | Double |  | VAV | Gas | 0.0066635 | 0.00012474 | -1.062e-09 | 5.4819 | 0.0025477 | -1.718e-07
12 | Double | Single |  | VAV | Gas | 0.025788 | 8.6472e-05 | -6.27e-10 | 3.0243 | 0.001035 | -4.63e-08
Peak Load Reduction Regressions | [5 empty] | Regression Form (a+bx+cx^2)
[6 empty] | Base Peak Load Coefficient |  |  | Cooling Coefficients
No. | Base | HVAC Type | CSW Type | Fuel |  | a | b | c | a | b | c
1 | Single | VAV | Single | N/A |  | 23.1195 | 0.0061556 | -6.276e-07 | 21.1987 | 0.0056719 | -4.592e-07
2 | Single | VAV | Double | N/A |  | 23.0244 | 0.0060725 | -5.973e-07 | 40.881 | 0.0063162 | -4.52e-08
3 | Double | VAV | Single | N/A |  | 20.816 | 0.0054447 | -4.64e-07 | 13.1679 | 0.0036668 | -3.665e-07
4 | Single | FCU | Single | N/A |  | 23.1195 | 0.0061556 | -6.276e-07 | 21.1987 | 0.0056719 | -4.592e-07
5 | Single | FCU | Double | N/A |  | 23.0244 | 0.0060725 | -5.973e-07 | 40.881 | 0.0063162 | -4.52e-08
6 | Double | FCU | Single | N/A |  | 20.816 | 0.0054447 | -4.64e-07 | 13.1679 | 0.0036668 | -3.665e-07
Baseline EUI Regressions | [5 empty] | Regression Form (a+bx+cx^2)
Coefficients
No. | Base | CSW Type |  | HVAC Type | Fuel | a | b | c
1 | Single | N/A |  | VAV | Elec | 50.1109 | -0.0019976 | 6.983e-07
2 | Double | N/A |  | VAV | Elec | 48.2583 | -0.0023833 | 6.748e-07
3 | Single | N/A |  | VAV | Gas | 50.6134 | -0.0014571 | 7.744e-07
4 | Double | N/A |  | VAV | Gas | 48.767 | -0.0019935 | 7.509e-07
5 | Single | N/A |  | FCU | Elec | 34.7028 | 0.00039535 | 5.551e-07
6 | Double | N/A |  | FCU | Elec | 33.3119 | 0.00035673 | 4.938e-07
7 | Single | N/A |  | FCU | Gas | 36.0445 | 0.00018573 | 6.944e-07
8 | Double | N/A |  | FCU | Gas | 35.7159 | -0.00032935 | 6.558e-07

## Regresson List_SS
Energy Savings Regressions | [5 empty] | Regression Form (a+bx+cx^2)
[6 empty] | Heating Coefficients |  |  | Cooling Coefficients |  |  | Notes/Assumptions (change from red to black when coefficients are dialed in)
No. | Base | CSW Type |  | HVAC Type | Fuel | a | b | c | a | b | c
1 | Single | Single |  | FCU | Elec | 0.07667 | 0.0023295 | -1.4e-09 | 1.0341 | 0.00022722 | -6e-10
2 | Single | Double |  | FCU | Elec | 0.16046 | 0.0021483 | -5.3467e-09 | 1.4756 | 0.00086338 | -2.23e-08
3 | Double | Single |  | FCU | Elec | 0.013688 | 0.001141 | 1.15e-08 | 0.87462 | 0.00019487 | -1.7e-09
4 | Single | Single |  | VAV | Elec | 0.30646 | 0.0032212 | -2.0506e-08 | 3.7648 | 0.001538 | -9.924e-08
5 | Single | Double |  | VAV | Elec | 0.26912 | 0.0030125 | -2.7017e-08 | 6.0997 | 0.0029145 | -2.0178e-07
6 | Double | Single |  | VAV | Elec | 0.60649 | 0.0021689 | -4.0728e-09 | 3.118 | 0.0011289 | -3.6959e-08
7 | Single | Single |  | FCU | Gas | 0.00327 | 9.9355e-05 | -5.97e-11 | 1.0341 | 0.00022722 | -6e-10
8 | Single | Double |  | FCU | Gas | 0.0068438 | 9.1624e-05 | -2.28e-10 | 1.4756 | 0.00086338 | -2.23e-08
9 | Double | Single |  | FCU | Gas | 0.0005838 | 4.8664e-05 | 4.905e-10 | 0.87462 | 0.00019487 | -1.7e-09
10 | Single | Single |  | VAV | Gas | 0.013071 | 0.00013738 | -8.746e-10 | 3.7648 | 0.001538 | -9.924e-08
11 | Single | Double |  | VAV | Gas | 0.011478 | 0.00012849 | -1.1523e-09 | 6.0997 | 0.0029145 | -2.0178e-07
12 | Double | Single |  | VAV | Gas | 0.030167 | 9.1132e-05 | -8.22e-11 | 3.118 | 0.0011289 | -3.6959e-08
Peak Load Reduction Regressions | [5 empty] | Regression Form (a+bx+cx^2)
[6 empty] | Base Peak Load Coefficient |  |  | Cooling Coefficients
No. | Base | HVAC Type | CSW Type | Fuel |  | a | b | c | a | b | c
1 | Single | VAV | Single | N/A |  | 14.0663 | 0.0051478 | -5.317e-07 | 18.6274 | 0.0062097 | -6.352e-07
2 | Single | VAV | Double | N/A |  | 13.259 | 0.0058206 | -6.029e-07 | 37.7857 | 0.0078383 | -6.158e-07
3 | Double | VAV | Single | N/A |  | 12.3843 | 0.0049067 | -4.9e-07 | 12.5508 | 0.0030735 | -2.484e-07
4 | Single | FCU | Single | N/A |  | 14.0663 | 0.0051478 | -5.317e-07 | 18.6274 | 0.0062097 | -6.352e-07
5 | Single | FCU | Double | N/A |  | 13.259 | 0.0058206 | -6.029e-07 | 37.7857 | 0.0078383 | -6.158e-07
6 | Double | FCU | Single | N/A |  | 12.3843 | 0.0049067 | -4.9e-07 | 12.5508 | 0.0030735 | -2.484e-07
Baseline EUI Regressions | [5 empty] | Regression Form (a+bx+cx^2)
Coefficients
No. | Base | CSW Type |  | HVAC Type | Fuel | a | b | c
1 | Single | N/A |  | VAV | Elec | 53.562 | -0.0013443 | 1.1176e-06
2 | Double | N/A |  | VAV | Elec | 52.0153 | -0.0017659 | 1.0907e-06
3 | Single | N/A |  | VAV | Gas | 53.9476 | -0.00045128 | 1.2431e-06
4 | Double | N/A |  | VAV | Gas | 52.3491 | -0.00076439 | 1.1884e-06
5 | Single | N/A |  | FCU | Elec | 46.581 | -0.0009915 | 1.1638e-06
6 | Double | N/A |  | FCU | Elec | 45.9373 | -0.0016372 | 1.1558e-06
7 | Single | N/A |  | FCU | Gas | 47.0639 | -0.00053891 | 1.3252e-06
8 | Double | N/A |  | FCU | Gas | 46.471 | -0.0013285 | 1.3182e-06
Cooling / Aux Split Regression |  |  | a | b | c | d
| VAV |  | 0.54363 | -0.0002672 | 6.9504e-08 | -7e-12
| FCU |  | 0.94835 | -0.00023927 | 5.443e-09 | 1e-12

## Regresson List_Hosp
Energy Savings Regressions | [5 empty] | Regression Form (a+bx+cx^2)
[6 empty] | Heating Coefficients |  |  | Cooling Coefficients |  |  | Notes/Assumptions
No. | Base | CSW Type |  | HVAC Type | Fuel | a | b | c | a | b | c
1 | Single | Single |  | VAV | Elec | 19.2535 | 0.0021028 | -2.52e-08 | 8.3588 | 0.0051741 | -4.5098e-07 |  | -0.27284 | 0.0039845 | -2.1953e-07 | 1.5741 | 0.0081792 | -4.4986e-06
2 | Single | Double |  | VAV | Elec | 26.1154 | 0.0017024 | -1.44e-08 | 10.0933 | 0.0072545 | -6.7343e-07 |  | 0.074575 | 0.003999 | -2.8628e-07 | 0.78588 | 0.0092962 | -5.2852e-06
3 | Double | Single |  | VAV | Elec | 13.5118 | 0.00071769 | 2.8786e-09 | 3.6366 | 0.0042105 | -3.3164e-07 |  | 2.4796 | 0.0030728 | -1.6648e-07 | 1.6499 | 0.012552 | -6.349e-06
4 | Single | Single |  | VAV | Gas | 0.80257 | 9.1983e-05 | -1.2e-09 | 8.3588 | 0.0051741 | -4.5098e-07 |  | 2.2479 | 0.0021615 | -1.5232e-07 | 0.45658 | 0.017916 | -1.0135e-05
5 | Single | Double |  | VAV | Gas | 1.1203 | 7.3165e-05 | -3e-10 | 10.0933 | 0.0072545 | -6.7343e-07 |  | 0.02227 | 0.00015822 | -8.428e-09 | 1.2666 | 0.0088125 | -4.7465e-06
6 | Double | Single |  | VAV | Gas | 0.57628 | 3.0609e-05 | -1.228e-10 | 3.6366 | 0.0042105 | -3.3164e-07 |  | -1.0558 | 0.00047562 | -3.4052e-08 | 0.78682 | 0.0092579 | -5.1559e-06
[13 empty] | -0.19323 | 0.00021308 | -1.1548e-08 | 0.8344 | 0.016489 | -8.9439e-06
Peak Load Reduction Regressions | [5 empty] | Regression Form (a+bx+cx^2) | [6 empty] | -0.093324 | 0.00015414 | -1.1003e-08 | 0.45982 | 0.017847 | -9.932e-06
[6 empty] | Base Peak Load Coefficient |  |  | Cooling Coefficients
No. | Base | HVAC Type | CSW Type | Fuel |  | a | b | c | a | b | c
1 | Single | VAV | Single | N/A |  | 15.9452 | 0.0062549 | -4.666e-07 | 10.2212 | 0.004944 | -4.35e-07
2 | Single | VAV | Double | N/A |  | 15.9452 | 0.0062549 | -4.666e-07 | 16.1958 | 0.010505 | -1.0237e-06
3 | Double | VAV | Single | N/A |  | 19.62 | 0.003158 | -2.394e-07 | 5.1435 | 0.003977 | -3.869e-07
Baseline EUI Regressions | [5 empty] | Regression Form (a+bx+cx^2)
Coefficients
No. | Base | CSW Type |  | HVAC Type | Fuel | a | b | c
1 | Single | N/A |  | VAV | Elec | 222.3254 | -0.008719 | 1.229e-06
2 | Double | N/A |  | VAV | Elec | 217.221 | -0.0080141 | 1.1096e-06
3 | Single | N/A |  | VAV | Gas | 238.563 | -0.0081294 | 1.3234e-06
4 | Double | N/A |  | VAV | Gas | 229.9586 | -0.0063651 | 1.1099e-06
Cooling / Aux Split Regression |  |  | a | b | c | d
|  |  | 0.71341 | -0.00019542 | 3.9398e-08 | -3e-12

## Regresson List_MF
Energy Savings Regressions | [6 empty] | Regression Form (a+bx+cx^2)
[7 empty] | Heating Coefficients |  |  | Cooling Coefficients |  |  | Notes/Assumptions
No. | Base | SGS Type | MF Type | HVAC/Fuel Type | Location | Occ | a | b | c | a | b | c
1 | Single | Single | Low | PTAC_Elec |  |  | 0.299 | 0.0025234 | 2.3682e-08 | 2.5605 | 0.0019479 | -6e-08
2 | Single | Double | Low | PTAC_Elec |  |  | 0.28229 | 0.0015466 | 9.7967e-08 | 4.7841 | 0.0037555 | -1.745e-07
3 | Double | Single | Low | PTAC_Elec |  |  | 0.10639 | 0.0011628 | 7.3912e-09 | 1.2302 | 0.0018858 | -8.9e-08
4 | Single | Single | Mid | FCU_Elec |  |  | 0.16121 | 0.0021418 | 4.2685e-08 | 2.4323 | 0.001554 | -5.8284e-08
5 | Single | Double | Mid | FCU_Elec |  |  | 0.14207 | 0.0012868 | 1.0679e-07 | 4.5673 | 0.0034876 | -2.2003e-07
6 | Double | Single | Mid | FCU_Elec |  |  | 0.058778 | 0.00076818 | 3.9601e-08 | 1.1837 | 0.0015549 | -8.4302e-08
7 | Single | Single | Mid | FCU_Gas |  |  | 0.0068754 | 9.1347e-05 | 1.8205e-09 | 2.4323 | 0.001554 | -5.8284e-08
8 | Single | Double | Mid | FCU_Gas |  |  | 0.0060592 | 5.4883e-05 | 4.5544e-09 | 4.5673 | 0.0034876 | -2.2003e-07
9 | Double | Single | Mid | FCU_Gas |  |  | 0.0025069 | 3.2763e-05 | 1.689e-09 | 1.1837 | 0.0015549 | -8.4302e-08
Peak Load Reduction Regressions | [5 empty] | Regression Form (a+bx+cx^2)
[6 empty] | Baseline Cooling Load Coefficients |  |  | Cooling Coefficients
No. | Base | MF Type | SGS Type | Fuel |  | a | b | c | a | b | c
1 | Single | Low | Single | N/A |  | 12.5835 | 0.0032441 | -2.879e-07 | 23.4622 | 0.0062223 | -6.095e-07
2 | Single | Low | Double | N/A |  | 12.5835 | 0.0032441 | -2.879e-07 | 50.0156 | 0.0060901 | -4.273e-07
3 | Double | Low | Single | N/A |  | 10.599 | 0.0025959 | -2.413e-07 | 18.2796 | 0.0021591 | -2.9e-08
4 | Single | Mid | Single | N/A |  | 10.3001 | 0.0027499 | -1.929e-07 | 16.6972 | 0.0055256 | -4.957e-07
5 | Single | Mid | Double | N/A |  | 10.3001 | 0.0027499 | -1.929e-07 | 34.8294 | 0.0084273 | -6.738e-07
6 | Double | Mid | Single | N/A |  | 8.7783 | 0.0021889 | -1.501e-07 | 11.1553 | 0 | -2.531e-07
Baseline EUI Regressions | [6 empty] | Regression Form (a+bx+cx^2)
[7 empty] | Heating Coefficients |  |  | Cooling Coefficients
No. | Base | SGS Type | MF Type | HVAC Type | Fuel |  | a | b | c | a | b | c
1 | Single | N/A | Low | PTAC | Elec |  | 50.1496 | -0.0039338 | 6.624e-07 | 50.1496 | -0.0039338 | 6.624e-07
2 | Double | N/A | Low | PTAC | Elec |  | 42.4892 | -0.002642 | 5.102e-07 | 42.4892 | -0.002642 | 5.102e-07
3 | Single | N/A | Mid | FCU | Elec |  | 47.6672 | -0.0038797 | 6.607e-07 | 47.6672 | -0.0038797 | 6.607e-07
4 | Double | N/A | Mid | FCU | Elec |  | 44.8676 | -0.0035527 | 5.671e-07 | 44.8676 | -0.0035527 | 5.671e-07
5 | Single | N/A | Mid | FCU | Gas |  | 47.7768 | -0.0034438 | 7.203e-07 | 47.7768 | -0.0034438 | 7.203e-07
6 | Double | N/A | Mid | FCU | Gas |  | 44.9531 | -0.0032699 | 6.227e-07 | 44.9531 | -0.0032699 | 6.227e-07
Savings Adjustment Factor Regressions
No. | Base | CSW Type | Single | HVAC | Fuel |  | a | b | c | d
1 | Single | Single | Low | PTAC | Elec |  | 0.86043 | -2.2759e-05 | 2.5496e-09 | -1e-13
2 | Single | Double | Low | PTAC | Elec |  | 0.86043 | -2.2759e-05 | 2.5496e-09 | -1e-13
3 | Double | Single | Low | PTAC | Elec |  | 0.86043 | -2.2759e-05 | 2.5496e-09 | -1e-13
4 | Single | Single | Mid | FCU | Elec |  | 0.86043 | -2.2759e-05 | 2.5496e-09 | -1e-13
5 | Single | Double | Mid | FCU | Elec |  | 0.86043 | -2.2759e-05 | 2.5496e-09 | -1e-13
6 | Double | Single | Mid | FCU | Elec |  | 0.86043 | -2.2759e-05 | 2.5496e-09 | -1e-13
7 | Single | Single | Mid | FCU | Gas |  | 0.86043 | -2.2759e-05 | 2.5496e-09 | -1e-13
8 | Single | Double | Mid | FCU | Gas |  | 0.86043 | -2.2759e-05 | 2.5496e-09 | -1e-13
9 | Double | Single | Mid | FCU | Gas |  | 0.86043 | -2.2759e-05 | 2.5496e-09 | -1e-13
Savings Adjustment Factor Regressions (Cool)
No. | Base | CSW Type | MF Type | HVAC | Fuel |  | a | b | c | d
1 | Single | Single | Low | PTAC | Elec |  | 0.96487 | -4.3579e-05 | 1.028e-08 | -1e-12
2 | Single | Double | Low | PTAC | Elec |  | 0.96487 | -4.3579e-05 | 1.028e-08 | -1e-12
3 | Double | Single | Low | PTAC | Elec |  | 0.96487 | -4.3579e-05 | 1.028e-08 | -1e-12
4 | Single | Single | Mid | FCU | Elec |  | 0.96487 | -4.3579e-05 | 1.028e-08 | -1e-12
5 | Single | Double | Mid | FCU | Elec |  | 0.96487 | -4.3579e-05 | 1.028e-08 | -1e-12
6 | Double | Single | Mid | FCU | Elec |  | 0.96487 | -4.3579e-05 | 1.028e-08 | -1e-12
7 | Single | Single | Mid | FCU | Gas |  | 0.96487 | -4.3579e-05 | 1.028e-08 | -1e-12
8 | Single | Double | Mid | FCU | Gas |  | 0.96487 | -4.3579e-05 | 1.028e-08 | -1e-12
9 | Double | Single | Mid | FCU | Gas |  | 0.96487 | -4.3579e-05 | 1.028e-08 | -1e-12
Cooling Adjustment Regressoins Regressions | [6 empty] | a | b | c | d
Mid-size | [6 empty] | 0.86172 | -0.00029049 | 7.5e-08 | -1e-11
Low-rise | [6 empty] | 0.64499 | -0.00035283 | 9.583e-08 | -1e-11

## Lists
Type of Glass | State | Alabama | Alaska | Arizona | Arkansas | California | Colorado | Connecticut | Delaware | Florida | Georgia | Hawaii | Idaho | Illinois | Indiana | Iowa | Kansas | Kentucky | Louisiana | Maine | Maryland | Massachusetts | Michigan | Minnesota | Mississippi | Missouri | Montana | Nebraska | Nevada | New_Hampshire | New_Jersey | New_Mexico | New_York | North_Carolina | North_Dakota | Ohio | Oklahoma | Oregon | Pennsylvania | Rhode_Island | South_Carolina | South_Dakota | Tennessee | Texas | Utah | Vermont | Virginia | Washington | West_Virginia | Wisconsin | Wyoming | Dist._of_Columbia | SGS Type | Fuel | HVAC Type, Office | Building Type | Occ | Infil | Cooling
Single pane | Alabama | Anniston | Adak | Casa Granda | Batesville | Alturas | Akron CO | Danbury | Dover | Crestview | Albany GA | Hilo | Boise | Aurora IL | Bloomington IN | Algona | Chanute | Bowling Green | Alexandria LA | Auburn ME | Baltimore | Beverly | Alpena | Aitkin | Biloxi | Cape Girardeau | Billings | Ainsworth | Elko | Berlin | Atlantic City | Alamogordo | Albany NY | Asheville | Bismarck | Akron OH | Altus | Astoria | Allentown | New Shoreham | Anderson | Aberdeen SD | Blountville | Abilene | Blanding | Burlington VT | Abingdon | Aberdeen WA | Beckley | Antigo | Casper | Washington DC | Single | Electric | Packaged VAV with electric reheat | Office | 33% | Included | Yes
Double pane | Alaska | Auburn AL | Anchorage | Douglas | Bentonville | Bakersfield | Alamosa | Groton | Wilmington DE | Daytona | Alma | Honolulu | Burley | Belleville | Evansville | Atlantic | Concordia | Fort Knox | Baton Rouge | Augusta ME | Camp Springs | Boston | Ann Arbor | Albert Lea | Columbus MS | Columbia MO | Bozeman | Alliance | Ely | Concord NH | Belmar | Albuquerque | Binghamton | Cape Hatteras | Devils Lake | Cincinnati | Bartlesville | Aurora OR | Altoona | Pawtucket | Beaufort | Brookings | Chattanooga | Alice | Bryce Canyon City | Montpelier | Blacksburg | Bellingham | Bluefield | Appleton | Cheyenne |  | Double | Natural Gas | Packaged VAV with hydronic reheat | Hotel | 66% | Excluded | No
New double pane (U<0.35) | Arizona | Birmingham | Aniak | Flagstaff | El Dorado | Bishop | Aspen | Hartford Brainard |  | Fort Lauderdale | Athens | Kahului | Caldwell | Bloomington IL | Fort Wayne | Boone | Dodge City | Hebron | Bossier City | Bangor | Hagerstown | Chicopee Falls | Battle Creek | Alexandria MN | Greenville MS | Farmington MO | Butte | Beatrice | Fallon | Keene | Fairfield NJ | Carlsbad NM | Buffalo | Charlotte | Dickinson | Cleveland | Clinton OK | Baker City | Bradford | Providence | Charleston SC | Huron | Crossville | Amarillo | Cedar City | Rutland | Charlottesville | Bremerton | Bridgeport | Eau Claire | Cody |  |  | None | Built-up VAV with hydronic reheat | Primary School | 100%
| Arkansas | Daleville | Annette Island | Grand Canyon | Fayetteville AR | Blue Canyon | Aurora CO | New Haven |  | Fort Myers | Atlanta | Kalaoa | Coeur d'Alene | Bondville | Huntingburg | Burlington IA | Emporia | Henderson City | Houma | Bar Harbor | Lexington Park | Hyannis | Benton Harbor | Austin MN | Greenwood | Ft. Leonard Wood | Cut Bank | Bellevue | Las Vegas NV | Laconia | Millville | Clayton | Elmira | Elizabeth City | Fargo | Columbus OH | Enid | Burns | Butler |  | Columbia SC | Mitchell | Dyersburg | Austin TX | Delta | Springfield VT | Danville | Ephrata | Charleston WV | Green Bay | Evanston |  |  |  | Other | Secondary School
| California | Dothan | Anvik | Kingman | Flippin | Blythe | Broomfield | Oxford |  | Fort Pierce | Augusta GA | Kaneohe | Grand View | Chicago | Indianapolis | Carroll | Garden City | Hopkinsville | Lafayette LA | Brunswick ME | Salisbury | Lawrence | Cadillac | Baudette | Gulfport | Jefferson City | Glasgow | Broken Bow | Lovelock | Lebanon | Newark | Clovis | Glen Falls | Fayetteville NC | Grand Forks | Dayton | Fort Sill | Corvallus | DuBois |  | Florence | Mobridge | Jackson TN | Brownsville | Hanksville |  | Farmville | Everett | Elkins | Janesville | Gillette |  |  | Electric Only |  | Hospital
| Colorado | Gadsen | Big River Lakes | Luke | Fort Smith | Burbank | Colorado Springs | Stratford |  | Gainesville | Brunswick GA | Kapalua | Hailey | Decatur | Kokomo | Cedar Rapids | Goodland | Jackson KY | Lake Charles | Caribou |  | Marthas Vineyard | Calumet | Bemidji | Hattiesburg | Joplin | Glendive | Chadron | Mercury | Manchester | Rio Grande | Deming | Jamestown NY | Goldsboro | Jamestown ND | Findlay | Gage | Eugene | Erie |  | Greenville SC | Pierre | Knoxville TN | Childress | Moab |  | Franklin VA | Forks | Huntington | La Cross | Jackson Hole |  |  | Electric | HVAC Type, Hotel | Multi-family
| Connecticut | Huntsville | Birchwood | Page | Harrison | Camarillo | Cortez |  |  | Homestead | Columbus GA | Kapolei | Idaho Falls | Marion IL | Lafayette IN | Chariton | Great Bend | Lexington | Leesville | Frenchville |  | Mashpee | Detroit | Benson | Jackson MS | Kaiser | Great Falls | Columbus NE | Reno | Mount Washington | Teterboro | Farmington NM | Massena | Greensboro | Minot | Mansfield | Hobart | Klamath Falls | Franklin PA |  | Greer | Rapid City | Memphis | College Station | Ogden |  | Fredericksburg | Hanford | Lewisburg | Lone Rock | Lander |  |  | None | PTAC | Other
| Delaware | Mobile | Chulitna | Phoenix | Hot Springs AR | Camp Pendleton | Craig |  |  | Jacksonville FL | Macon | Kapolei | Lewiston | Moline | Muncie | Charles City | Hays | London | Monroe | Houlton |  | Nantucket | Escanaba | Brainerd | McComb | Kansas City | Havre | Falls City | Tonopah | Portsmouth | Trenton | Gallup | Monticello NY | Greenville NC | Williston | Toledo OH | Lawton | La Grande | Harrisburg |  | Myrtle Beach | Sioux Falls | Nashville | Corpus Christi | Provo |  | Hampton | Hoquiam | Martinsburg | Madison | Laramie |  |  |  | PTHP
| Dist._of_Columbia | Montgomery | Cold Bay | Prescott | Jonesboro | Carlsbad CA | Denver |  |  | Key West | Marietta | Lanai | Malad City | Mount Vernon | South Bend | Clarinda | Hill City | Louisville | New Iberia | Millinocket |  | New Bedford | Flint | Cambridge | Meridian | Kirksville | Helena | Fremont | Winnemucca |  |  | Las Cruces | New Windsor | Havelock |  | Youngstown | McAlester | Lakeview | Johnstown |  | North Myrtle Beach | Watertown SD |  | Cotulla | Saint George |  | Hillsville | Kelso | Morgantown | Manitowac | Rawlins |  |  |  | Fan Coil Unit
| Florida | Muscle Shoals | Cordova | Safford | Little Rock | Chino | Durango |  |  | Lakeland | Rome | Lihue | Pocatello | Murphysboro | Terre Haute | Clinton IA | Hutchinson KS | Somerset | New Orleans | Portland ME |  | North Adams | Freeland | Cloquet | Natchez | Poplar Bluff | Kalispell | Grand Island |  |  |  | Las Vegas NM | New York | Hickory |  | Zanesville | Oklahoma City | Medford | Lancaster PA |  | Sumter | Yankton |  | Dalhart | Salt Lake City |  | Hot Springs VA | Moses Lake | parkersburg | Marshfield | Riverton |  |  |  | Other
| Georgia | Troy | Dillingham | Scottsdale | Pine Bluff | Chula Vista | Fort Collins |  |  | Marathon | Savannah | Molokai | Salmon | Peoria |  | Council Bluffs | Junction City | West Paducah | Patterson | Presque Isle |  | Norwood | Grand Rapids MI | Crane Lake | Starkville | Springfield MO | Lewistown | Hastings |  |  |  | Roswell | Nigara Falls | Jacksonville NC |  |  | Ponca City | North Bend | Middletown |  |  |  |  | Dallas | Vernal |  | Leesburg | Olympia | Wheeling | Milwaukee | Rock Springs
| Hawaii | Tuscaloosa | Dutch Harbor | Show Low | Rogers | Concord CA | Grand Junction |  |  | Mayport | Valdosta |  | Soda Springs | Quincy |  | Creston | Liberal |  | Pineville | Rockland |  | Plymouth | Houghton Lake | Crookston | Tupelo | St. Joseph | Livingston | Holdrege |  |  |  | Ruidoso | Republic | Kinston |  |  | Stillwater | Pendleton | Philadelphia |  |  |  |  | Del Rio | Wendover |  | Lynchburg | Pasco |  | Minocqua | Sheridan |  |  |  | HVAC Type, School
| Idaho |  | Emmonak | Tucson | Siloam Spring | Crescent City | Greeley |  |  | Melbourne | Warner Robins |  | Twin Falls | Rock Falls |  | Decorah | Manhattan |  | Shreveport | Sanford |  | Provincetown | Howell | Detroit Lakes |  | St. Louis | Miles City | Imperial NE |  |  |  | Santa Fe | Rockester | Manteo |  |  | Tulsa | Portland OR | Pittsburgh |  |  |  |  | El Paso |  |  | Manassas | Port Angeles |  | Mosinee | Workland |  |  |  | Central Ducted VAV
| Illinois |  | Fairbanks | Winslow | Springdale | Daggett | Gunnison |  |  | Miami |  |  |  | Rockford |  | Denison | Newton KS |  |  | Waterville |  | Westfield | Ironwood | Duluth |  | Vichy | Missoula | Kearney |  |  |  | Taos | Ronkonkoma | New Bern |  |  |  | Redmond | Reading |  |  |  |  | Galveston |  |  | Marion VA | Pullman |  | Oshkosh |  |  |  |  | Fan Coil Unit
| Indiana |  | Gustavus | Yuma | Stuttgart | Fairfield CA | Gypsum |  |  | Milton |  |  |  | Springfield IL |  | Des Moines | Olathe |  |  | Wiscasset |  | Worchester | Jackson MI | Ely |  | Warrensburg | Sidney MT | Lincoln |  |  |  | Truth or Consequences | Saranac Lake | Raleigh |  |  |  | Roseburg | Scranton |  |  |  |  | Georgetown |  |  | Martinsville | Renton |  | Phillips |  |  |  |  | Other
| Iowa |  | Healy |  | Texarkana | Fresno | Hayden |  |  | Naples |  |  |  | West Chicago |  | Dubuque | Russell | [5 empty] | Kalamazoo | Eveleth |  |  | Wolf Point | McCook |  |  |  | Tucumcari | Syracuse | Rocky Mount |  |  |  | Salem | University Park |  |  |  |  | Greenville TX |  |  | Melfa | Seattle |  | Rhinelander
| Kansas |  | Homer |  | Walnut Ridge | Fullerton | La Junta |  |  | Ocala | [5 empty] | Estherville | Salina | [5 empty] | Kincheloe | Fairmont |  |  |  | Norfolk NE |  |  |  |  | Utica | Southern Pines |  |  |  | Sexton Summit | Washington PA |  |  |  |  | Harlingen |  |  | Newport News | Spokane |  | Rice Lake |  |  |  |  | Packaged VAV with electric reheat | PVAV_Elec
| Kentucky |  | Hoonah |  |  | Hawthorne | Lakewood |  |  | Orlando | [5 empty] | Fairfield IA | Topeka | [5 empty] | Kingsford | Faribault |  |  |  | North Platte |  |  |  |  | Wappingers Falls | Wilmington NC |  |  |  |  | Williamsport |  |  |  |  | Hondo |  |  | Norfolk VA | Stampede Pass |  | Sturgeon Bay |  |  |  |  | Packaged VAV with hydronic reheat | PVAV
| Louisiana |  | Hooper Bay |  |  | Hayward | Lamar |  |  | Panama City | [5 empty] | Fort Dodge | Wichita | [5 empty] | Lansing | Fergus Falls |  |  |  | Omaha |  |  |  |  | Watertown NY | Winston-Salem | [9 empty] | Houston |  |  | Petersburg VA | Tacoma |  | Watertown WI |  |  |  |  | Built-up VAV with hydronic reheat | VAV
| Maine |  | Huslia |  |  | Imperial CA | Leadville |  |  | Pensacola | [5 empty] | Fort Madison | [6 empty] | Manistee | Flying Cloud |  |  |  | O'Neill |  |  |  |  | Westhampton Beach | [10 empty] | Killeen |  |  | Pulaski | The Dalles |  | Wausau |  |  |  |  | Central Ducted VAV | VAV
| Maryland |  | Iliamna |  |  | Lancaster CA | Limon |  |  | Sarasota | [5 empty] | Keokuk | [6 empty] | Marie | Fosston |  |  |  | Ord |  |  |  |  | White Plains | [10 empty] | Kingsville |  |  | Quantico | Toledo WA | [6 empty] | PTAC | PTAC
| Massachusetts |  | Juneau |  |  | Lemoore | Montrose |  |  | St. Petersburg | [5 empty] | Knoxville IA | [6 empty] | Menominee | Glenwood |  |  |  | Scottsbluff | [15 empty] | Laredo |  |  | Richmond | Walla Walla | [6 empty] | PTHP | PTHP
| Michigan |  | Kake |  |  | Livermore | Pueblo |  |  | Tallahasse | [5 empty] | Le Mars | [6 empty] | Mount Clemens | Grand Rapids MN |  |  |  | Sidney NE | [15 empty] | Longview |  |  | Roanoke | Wenatchee | [6 empty] | Fan Coil Unit | FCU
| Minnesota |  | Kenai |  |  | Lompoc | Rifle |  |  | Tampa | [5 empty] | Mason City | [6 empty] | Muskegon | Hallock |  |  |  | Tekamah | [15 empty] | Lubbock |  |  | Virginia Beach | Whidbey Island | [6 empty] | Other | FCU
| Mississippi |  | Ketchikan |  |  | Long Beach | Trinidad |  |  | Vero Beach | [5 empty] | Monticello IA | [6 empty] | Oscoda | Hibbing |  |  |  | Valentine | [15 empty] | Lufkin |  |  | Weyers Cave | Yakima
| Missouri |  | King Salmon |  |  | Los Angeles |  |  |  | West Palm Beach | [5 empty] | Muscatine | [6 empty] | Pellston | Hutchinson | [19 empty] | Marfa |  |  | Winchester
| Montana |  | Kodiak |  |  | McKinleyville | [9 empty] | Newton IA | [6 empty] | Port Huron | International Falls | [19 empty] | McAllen |  |  | Wise | [7 empty] | HVAC Type, Hospital
| Nebraska |  | Mekoryuk |  |  | Merced | [9 empty] | Oelwen | [6 empty] | Traverse City | Litchfield | [19 empty] | McGregor | [10 empty] | Central Ducted VAV | VAV
| Nevada |  | Middleton Island |  |  | Modesto | [9 empty] | Orange City | [6 empty] | Waterford Township | Little Falls | [19 empty] | Midland | [10 empty] | Other | VAV
| New_Hampshire |  | Palmer |  |  | Montague | [9 empty] | Ottumwa | [7 empty] | Mankato | [19 empty] | Mineral wells
| New_Jersey |  | Petersburg AK |  |  | Monterey | [9 empty] | Red Oak | [7 empty] | Marshall | [19 empty] | Nacogdockes | [10 empty] | HVAC Type, Mid-rise Multi-family
| New_Mexico |  | Point Heiden |  |  | Napa | [9 empty] | Sheldon | [7 empty] | Minneapolis | [19 empty] | Palacios | [10 empty] | Fan Coil Unit
| New_York |  | Saint Mary's |  |  | Needles | [9 empty] | Shenandoah | [7 empty] | Mora | [19 empty] | Paris | [10 empty] | Other
| North_Carolina |  | Sand Point |  |  | Oakland | [9 empty] | Sioux City | [7 empty] | Morris | [19 empty] | Port Arthur
| North_Dakota |  | Seward |  |  | Oxnard | [9 empty] | Spencer | [7 empty] | New Ulm | [19 empty] | Rockport | [10 empty] | HVAC Type, Low-rise Multi-family
| Ohio |  | Sitka Japonski |  |  | Palm Springs | [9 empty] | Storm Lake | [7 empty] | Orr | [19 empty] | San Angelo | [10 empty] | PTAC
| Oklahoma |  | Skagway |  |  | Palmdale | [9 empty] | Washington IA | [7 empty] | Owatonna | [19 empty] | San Antonio | [10 empty] | Other
| Oregon |  | Soldotna |  |  | Paso Robles | [9 empty] | Waterloo | [7 empty] | Park Rapids | [19 empty] | Temple
| Pennsylvania |  | St. Paul |  |  | Porterville | [9 empty] | Webster City | [7 empty] | Pipestone | [19 empty] | Tyler
| Rhode_Island |  | Talkeetna |  |  | Red Bluff | [17 empty] | Red Wing | [19 empty] | Victoria
| South_Carolina |  | Togiac |  |  | Redding | [17 empty] | Redwood Falls | [19 empty] | Waco
| South_Dakota |  | Utqiagvik |  |  | Ridgecrest | [17 empty] | Rochester | [19 empty] | Wichita Falls
| Tennessee |  | Valdez |  |  | Riverside | [17 empty] | Roseau | [19 empty] | Wink
| Texas |  | Whittier |  |  | Sacremento | [17 empty] | Silver Bay
| Utah |  | Wrangell |  |  | Salinas | [17 empty] | St Cloud
| Vermont |  | Yakutat |  |  | San Diego | [17 empty] | St Paul
| Virginia |  |  |  |  | San Francisco | [17 empty] | Thief River Falls
| Washington |  |  |  |  | San Jose | [17 empty] | Two Harbors
| West_Virginia |  |  |  |  | San Luis Obispo | [17 empty] | Wheaton
| Wisconsin |  |  |  |  | Sandberg | [17 empty] | Willmar
| Wyoming |  |  |  |  | Santa Anna | [17 empty] | Winona
[6 empty] | Santa Barbara | [17 empty] | Worthington
Santa Maria
Santa Monica
Santa Rose
South Lake Tahoe
Stockton
Truckee
Twentynine Palms
Ukiah
Van Nuys
Visalia
Yuba City

## Weather Information
State | Cities | Heating Degree Days (HDD) | Cooling Degree Days (CDD)
Alabama | Anniston | 2585 | 1713
Alabama | Auburn AL | 2688 | 1477
Alabama | Birmingham | 2698 | 1912
Alabama | Daleville | 2447 | 2122
Alabama | Dothan | 2072 | 2443
Alabama | Gadsen | 3063 | 1383
Alabama | Huntsville | 3472 | 1701
Alabama | Mobile | 1724 | 2524
Alabama | Montgomery | 2183 | 2124
Alabama | Muscle Shoals | 2788 | 1701
Alabama | Troy | 2196 | 2217
Alabama | Tuscaloosa | 2656 | 2101
Aklaska | Adak | 9202 | 0
Aklaska | Anchorage | 10158 | 0
Aklaska | Aniak | 11513 | 0
Aklaska | Annette Island | 6865 | 11
Aklaska | Anvik | 11628 | 27
Aklaska | Big River Lakes | 9868 | 1
Aklaska | Birchwood | 9521 | 1
Aklaska | Chulitna | 10471 | 3
Aklaska | Cold Bay | 9517 | 0
Aklaska | Cordova | 9376 | 0
Aklaska | Dillingham | 10504 | 1
Aklaska | Dutch Harbor | 8963 | 0
Aklaska | Emmonak | 11775 | 0
Aklaska | Fairbanks | 13072 | 31
Aklaska | Gustavus | 9123 | 0
Aklaska | Healy | 10689 | 0
Aklaska | Homer | 9696 | 0
Aklaska | Hoonah | 8858 | 0
Aklaska | Hooper Bay | 11970 | 0
Aklaska | Huslia | 13574 | 0 | ???
Aklaska | Iliamna | 9855 | 8
Aklaska | Juneau | 8471 | 1
Aklaska | Kake | 8385 | 0
Aklaska | Kenai | 10071 | 5
Aklaska | Ketchikan | 8033 | 22
Aklaska | King Salmon | 10754 | 2
Aklaska | Kodiak | 8551 | 5
Aklaska | Mekoryuk | 11572 | 0
Aklaska | Middleton Island | 8285 | 0
Aklaska | Palmer | 8599 | 4
Aklaska | Petersburg AK | 8490 | 6
Aklaska | Port Heiden | 10084 | 0
Aklaska | Saint Mary's | 11770 | 0
Aklaska | Sand Point | 9143 | 0
Aklaska | Seward | 9112 | 0
Aklaska | Sitka Japonski | 8002 | 0
Aklaska | Skagway | 8379 | 9
Aklaska | Soldotna | 10146 | 3
Aklaska | St. Paul | 10607 | 0
Aklaska | Talkeetna | 10973 | 2
Aklaska | Togiac | 10391 | 3
Aklaska | Utqiagvik | 9862 | 0
Aklaska | Valdez | 9257 | 0
Aklaska | Whittier | 9362 | 1
Aklaska | Wrangell | 7985 | 5
Aklaska | Yakutat | 9117 | 0
Arizona | Casa Granda | 1473 | 3715
Arizona | Douglas | 2328 | 1832
Arizona | Flagstaff | 7112 | 110
Arizona | Grand Canyon | 6605 | 93
Arizona | Kingman | 3005 | 2444
Arizona | Luke | 1137 | 4152
Arizona | Page | 3658 | 1967
Arizona | Phoenix | 997 | 4591
Arizona | Prescott | 4146 | 1037
Arizona | Safford | 1891 | 2760
Arizona | Scottsdale | 1214 | 4065
Arizona | Show Low | 4515 | 643
Arizona | Tucson | 1596 | 3020
Arizona | Winslow | 4435 | 1247
Arizona | Yuma | 535 | 4532
Arkansas | Batesville | 3761 | 1687
Arkansas | Bentonville | 4394 | 1514
Arkansas | El Dorado | 2672 | 2512
Arkansas | Fayetteville AR | 3726 | 1753
Arkansas | Flippin | 3724 | 1604
Arkansas | Fort Smith | 3596 | 2020
Arkansas | Harrison | 3822 | 1590
Arkansas | Hot Springs AR | 3256 | 2111
Arkansas | Jonesboro | 4240 | 1934
Arkansas | Little Rock | 3079 | 2076
Arkansas | Pine Bluff | 3384 | 2460
Arkansas | Rogers | 4327 | 1669
Arkansas | Siloam Spring | 3868 | 1637
Arkansas | Springdale | 3963 | 1480
Arkansas | Stuttgart | 2833 | 2120
Arkansas | Texarkana | 2471 | 2486
Arkansas | Walnut Ridge | 3733 | 1731
California | Alturas | 6458 | 320
California | Bakersfield | 2013 | 2240
California | Bishop | 4053 | 1087
California | Blue Canyon | 5176 | 465
California | Blythe | 826 | 4527
California | Burbank | 1437 | 1449
California | Camarillo | 1979 | 342
California | Camp Pendleton | 2499 | 731
California | Carlsbad CA | 1798 | 272
California | Chino | 1609 | 1330
California | Chula Vista | 1642 | 410
California | Concord CA | 2484 | 785
California | Crescent City | 4884 | 0
California | Daggett | 1931 | 3036
California | Fairfield CA | 2708 | 1313
California | Fresno | 2327 | 2101
California | Fullerton | 1312 | 1187
California | Hawthorne | 1299 | 570
California | Hayward | 2327 | 131
California | Imperial CA | 837 | 4228
California | Lancaster CA | 2871 | 1983
California | Lemoore | 1654 | 1754
California | Livermore | 2933 | 679
California | Lompoc | 3256 | 27
California | Long Beach | 1136 | 995
California | Los Angeles | 1283 | 617
California | McKinleyville | 4964 | 4
California | Merced | 2268 | 1389
California | Modesto | 2211 | 1445
California | Montague | 5097 | 567
California | Monterey | 3218 | 64
California | Napa | 3186 | 191
California | Needles | 944 | 4672
California | Oakland | 2816 | 128
California | Oxnard | 2010 | 186
California | Palm Springs | 668 | 4333
California | Palmdale | 2829 | 1947
California | Paso Robles | 2558 | 852
California | Porterville | 2465 | 1620
California | Red Bluff | 2782 | 1868
California | Redding | 2694 | 1688
California | Ridgecrest | 2782 | 3004
California | Riverside | 1609 | 1413
California | Sacremento | 2581 | 1281
California | Salinas | 2852 | 84
California | San Diego | 1019 | 742
California | San Francisco | 2737 | 97
California | San Jose | 2301 | 395
California | San Luis Obispo | 2325 | 201
California | Sandberg | 3610 | 1089
California | Santa Anna | 1106 | 657
California | Santa Barbara | 2433 | 104
California | Santa Maria | 2795 | 32
California | Santa Monica | 1388 | 467
California | Santa Rose | 2859 | 329
California | South Lake Tahoe | 7847 | 11
California | Stockton | 2494 | 1296
California | Truckee | 7884 | 87
California | Twentynine Palms | 1788 | 3297
California | Ukiah | 2981 | 874
California | Van Nuys | 1214 | 1507
California | Visalia | 3032 | 1602
California | Yuba City | 2533 | 1476
Colorado | Akron CO | 6087 | 823
Colorado | Alamosa | 8528 | 23
Colorado | Aspen | 8294 | 68
Colorado | Aurora CO | 6093 | 825
Colorado | Broomfield | 5836 | 637
Colorado | Colorado Springs | 6115 | 481
Colorado | Cortez | 5921 | 523
Colorado | Craig | 8497 | 74
Colorado | Denver | 5655 | 923
Colorado | Durango | 7114 | 312
Colorado | Fort Collins | 7048 | 509
Colorado | Grand Junction | 5283 | 1230
Colorado | Greeley | 6792 | 484
Colorado | Gunnison | 9306 | 13
Colorado | Gypsum | 7853 | 116
Colorado | Hayden | 8169 | 211
Colorado | La Junta | 5194 | 1318
Colorado | Lakewood | 6112 | 582
Colorado | Lamar | 5635 | 1305
Colorado | Leadville | 10266 | 0
Colorado | Limon | 6576 | 373
Colorado | Montrose | 5984 | 746
Colorado | Pueblo | 5178 | 936
Colorado | Rifle | 5943 | 631
Colorado | Trinidad | 5266 | 798
Connecticut | Danbury | 6218 | 503
Connecticut | Groton | 5700 | 418
Connecticut | Hartford Brainard | 5969 | 731
Connecticut | New Haven | 5524 | 625
Connecticut | Oxford | 6425 | 551
Connecticut | Stratford | 5530 | 738
Delaware | Dover | 4987 | 1010
Delaware | Wilmington DE | 5087 | 1088
Florida | Crestview | 1672 | 2354
Florida | Daytona | 789 | 2857
Florida | Fort Lauderdale | 322 | 4114
Florida | Fort Myers | 205 | 4113
Florida | Fort Pierce | 722 | 2959
Florida | Gainesville | 1306 | 2659
Florida | Homestead | 318 | 4117
Florida | Jacksonville FL | 1281 | 2565
Florida | Key West | 67 | 4906
Florida | Lakeland | 973 | 3374
Florida | Marathon | 124 | 5280
Florida | Mayport | 1037 | 2806
Florida | Melbourne | 369 | 3269
Florida | Miami | 150 | 4292
Florida | Milton | 1728 | 2305
Florida | Naples | 289 | 3443
Florida | Ocala | 1144 | 2724
Florida | Orlando | 526 | 3234
Florida | Panama City | 1269 | 2877
Florida | Pensacola | 1174 | 2711
Florida | Sarasota | 604 | 3266
Florida | St. Petersburg | 429 | 3824
Florida | Tallahasse | 1545 | 2370
Florida | Tampa | 646 | 3442
Florida | Valparaiso | 2072 | 2339
Florida | Vero Beach | 299 | 3489
Florida | West Palm Beach | 316 | 3787
Georgia | Albany GA | 1739 | 2456
Georgia | Alma | 2097 | 2316
Georgia | Athens | 2730 | 1702
Georgia | Atlanta | 2773 | 1809
Georgia | Augusta GA | 2512 | 2023
Georgia | Brunswick GA | 2102 | 2568
Georgia | Columbus GA | 2063 | 2407
Georgia | Macon | 2400 | 2182
Georgia | Marietta | 3734 | 1401
Georgia | Rome | 3331 | 1895
Georgia | Savannah | 1759 | 2474
Georgia | Valdosta | 1525 | 2860
Georgia | Warner Robins | 2983 | 2069
Hawaii | Hilo | 0 | 3279
Hawaii | Honolulu | 0 | 4561
Hawaii | Kahului | 0 | 3999
Hawaii | Kalaoa | 0 | 4325
Hawaii | Kaneohe | 0 | 4485
Hawaii | Kapalua | 0 | 3908
Hawaii | Kapolei | 12 | 4410
Hawaii | Lanai | 22 | 2590
Hawaii | Lihue | 0 | 3919
Hawaii | Molokai | 97 | 3734
Idaho | Boise | 5395 | 756
Idaho | Burley | 6225 | 927
Idaho | Caldwell | 5803 | 636
Idaho | Coeur d'Alene | 6897 | 344
Idaho | Grand View | 6105 | 834
Idaho | Hailey | 7160 | 679
Idaho | Idaho Falls | 7769 | 246
Idaho | Lewiston | 5457 | 885
Idaho | Malad City | 6681 | 546
Idaho | Pocatello | 7100 | 393
Idaho | Salmon | 7482 | 309
Idaho | Soda Springs | 8439 | 198
Idaho | Twin Falls | 6148 | 733
Illinois | Aurora IL | 6790 | 683
Illinois | Belleville | 5320 | 1245
Illinois | Bloomington IL | 6112 | 847
Illinois | Bondville | 5747 | 1021
Illinois | Chicago | 6399 | 830
Illinois | Decatur | 5546 | 1166
Illinois | Marion IL | 4674 | 1330
Illinois | Moline | 6459 | 980
Illinois | Mount Vernon | 4817 | 1412
Illinois | Murphysboro | 4380 | 1633
Illinois | Peoria | 6229 | 888
Illinois | Quincy | 5233 | 1067
Illinois | Rock Falls | 6269 | 785
Illinois | Rockford | 7237 | 778
Illinois | Springfield IL | 5527 | 1166
Illinois | West Chicago | 6194 | 830
Indiana | Bloomington IN | 5385 | 1025
Indiana | Evansville | 4474 | 1376
Indiana | Fort Wayne | 6471 | 764
Indiana | Huntingburg | 4223 | 1448
Indiana | Indianapolis | 5845 | 1044
Indiana | Kokomo | 5957 | 822
Indiana | Lafayette IN | 5967 | 971
Indiana | Muncie | 5626 | 1004
Indiana | South Bend | 5956 | 860
Indiana | Terre Haute | 5135 | 1290
Iowa | Algona | 6847 | 707
Iowa | Atlantic | 6656 | 865
Iowa | Boone | 6699 | 897
Iowa | Burlington IA | 5680 | 1465
Iowa | Carroll | 6880 | 899
Iowa | Cedar Rapids | 6900 | 714
Iowa | Chariton | 6028 | 1252
Iowa | Charles City | 6765 | 733
Iowa | Clarinda | 6072 | 1319
Iowa | Clinton IA | 6895 | 1019
Iowa | Council Bluffs | 5864 | 969
Iowa | Creston | 6150 | 983
Iowa | Decorah | 6125 | 978
Iowa | Denison | 6571 | 1057
Iowa | Des Moines | 6493 | 1121
Iowa | Dubuque | 7516 | 525
Iowa | Estherville | 8458 | 551
Iowa | Fairfield IA | 6031 | 1093
Iowa | Fort Dodge | 7177 | 825
Iowa | Fort Madison | 5277 | 1148
Iowa | Keokuk | 5496 | 1208
Iowa | Knoxville IA | 5891 | 1265
Iowa | Le Mars | 6122 | 871
Iowa | Mason City | 7927 | 639
Iowa | Monticello IA | 6857 | 744
Iowa | Muscatine | 6206 | 1026
Iowa | Newton IA | 6207 | 816
Iowa | Oelwen | 6483 | 644
Iowa | Orange City | 6867 | 865
Iowa | Ottumwa | 6647 | 875
Iowa | Red Oak | 5959 | 1203
Iowa | Sheldon | 6939 | 723
Iowa | Shenandoah | 6233 | 1258
Iowa | Sioux City | 6796 | 936
Iowa | Spencer | 8206 | 592
Iowa | Storm Lake | 6982 | 821
Iowa | Washington IA | 6249 | 991
Iowa | Waterloo | 7257 | 827
Iowa | Webster City | 6376 | 1099
Kansas | Chanute | 4458 | 1804
Kansas | Concordia | 4890 | 1632
Kansas | Dodge City | 4969 | 1457
Kansas | Emporia | 5717 | 1458
Kansas | Garden City | 5180 | 1240
Kansas | Goodland | 5915 | 915
Kansas | Great Bend | 4891.5 | 1417
Kansas | Hays | 5021 | 1558
Kansas | Hill City | 5597 | 1192
Kansas | Hutchinson KS | 4591 | 1552
Kansas | Junction City | 4528 | 1600
Kansas | Liberal | 4810 | 1410
Kansas | Manhattan | 5013 | 1652
Kansas | Newton KS | 5023 | 1400
Kansas | Olathe | 4598 | 1437
Kansas | Russell | 5005 | 1436
Kansas | Salina | 4660 | 1787
Kansas | Topeka | 4953 | 1315
Kansas | Wichita | 4324 | 1554
Kentucky | Bowling Green | 4380 | 1410
Kentucky | Fort Knox | 4918 | 1283
Kentucky | Hebron | 5288 | 962
Kentucky | Henderson City | 5049 | 995
Kentucky | Hopkinsville | 4484 | 1620
Kentucky | Jackson KY | 3869 | 1098
Kentucky | Lexington | 4856 | 1104
Kentucky | London | 4529 | 988
Kentucky | Louisville | 4521 | 1449
Kentucky | Somerset | 3916 | 1550
Kentucky | West Paducah | 3811 | 1439
Louisiana | Alexandria LA | 1136 | 2477
Louisiana | Baton Rouge | 1762 | 2622
Louisiana | Bossier City | 2562 | 2270
Louisiana | Houma | 1677 | 2848
Louisiana | Lafayette LA | 1590 | 2699
Louisiana | Lake Charles | 1635 | 2596
Louisiana | Leesville | 2197 | 2514
Louisiana | Monroe | 2229 | 2270
Louisiana | New Iberia | 1717 | 2559
Louisiana | New Orleans | 1358 | 2784
Louisiana | Patterson | 1452 | 2571
Louisiana | Pineville | 2109 | 2421
Louisiana | Shreveport | 2351 | 2384
Maine | Auburn ME | 7691 | 303
Maine | Augusta ME | 7495 | 396
Maine | Bangor | 7671 | 450
Maine | Bar Harbor | 8037 | 71
Maine | Brunswick ME | 7456 | 373
Maine | Caribou | 9841 | 171
Maine | Frenchville | 9765 | 164
Maine | Houlton | 9255 | 206
Maine | Millinocket | 7921 | 323
Maine | Portland ME | 7679 | 335
Maine | Presque Isle | 9295 | 168
Maine | Rockland | 7451 | 194
Maine | Sanford | 7774 | 259
Maine | Waterville | 7926 | 367
Maine | Wiscasset | 6877 | 350
Maryland | Baltimore | 4631 | 1237
Maryland | Camp Springs | 4652 | 1178
Maryland | Hagerstown | 4867 | 1079
Maryland | Lexington Park | 3556 | 1404
Maryland | Salisbury | 3910 | 1229
Massachusetts | Beverly | 6669 | 492
Massachusetts | Boston | 5793 | 734
Massachusetts | Chicopee Falls | 6354 | 507
Massachusetts | Hyannis | 5749 | 436
Massachusetts | Lawrence | 5940 | 559
Massachusetts | Marthas Vineyard | 5622 | 361
Massachusetts | Mashpee | 6062 | 565
Massachusetts | Nantucket | 5350 | 298
Massachusetts | New Bedford | 5724 | 577
Massachusetts | North Adams | 6626 | 319
Massachusetts | Norwood | 6177 | 637
Massachusetts | Plymouth | 5889 | 374
Massachusetts | Provincetown | 5705 | 595
Massachusetts | Westfield | 6623 | 494
Massachusetts | Worchester | 7164 | 346
Michigan | Alpena | 8250 | 290
Michigan | Ann Arbor | 6487 | 492
Michigan | Battle Creek | 6210 | 639
Michigan | Benton Harbor | 6588 | 810
Michigan | Cadillac | 7905 | 373
Michigan | Calumet | 8988 | 239
Michigan | Detroit | 6621 | 679
Michigan | Escanaba | 8796 | 131
Michigan | Flint | 6977 | 515
Michigan | Freeland | 7059 | 524
Michigan | Grand Rapids MI | 6908 | 579
Michigan | Houghton Lake | 8067 | 316
Michigan | Howell | 6295 | 899
Michigan | Ironwood | 9090 | 348
Michigan | Jackson MI | 6385 | 715
Michigan | Kalamazoo | 6196 | 599
Michigan | Kincheloe | 9193 | 115
Michigan | Kingsford | 8327 | 432
Michigan | Lansing | 7045 | 597
Michigan | Manistee | 7343 | 582
Michigan | Marie | 9162 | 113
Michigan | Menominee | 7783 | 452
Michigan | Mount Clemens | 6040 | 597
Michigan | Muskegon | 7018 | 502
Michigan | Oscoda | 7315 | 455
Michigan | Pellston | 7426 | 360
Michigan | Port Huron | 6522 | 705
Michigan | Traverse City | 7754 | 370
Michigan | Waterford Township | 6152 | 772
Minnesota | Aitkin | 9304 | 194
Minnesota | Albert Lea | 7196 | 920
Minnesota | Alexandria MN | 8895 | 535
Minnesota | Austin MN | 7892 | 529
Minnesota | Baudette | 8804 | 112
Minnesota | Bemidji | 9161 | 333
Minnesota | Benson | 8676 | 659
Minnesota | Brainerd | 8713 | 322
Minnesota | Cambridge | 8823 | 405
Minnesota | Cloquet | 9368 | 258
Minnesota | Crane Lake | 10240 | 164
Minnesota | Crookston | 9095 | 348
Minnesota | Detroit Lakes | 8704 | 460
Minnesota | Duluth | 9620 | 159
Minnesota | Ely | 9501 | 186
Minnesota | Eveleth | 9987 | 255
Minnesota | Fairmont | 7586 | 652
Minnesota | Faribault | 7497 | 504
Minnesota | Fergus Falls | 7838 | 841
Minnesota | Flying Cloud | 7921 | 958
Minnesota | Fosston | 9746 | 252
Minnesota | Glenwood | 8440 | 528
Minnesota | Grand Rapids MN | 9137 | 306
Minnesota | Hallock | 9445 | 460
Minnesota | Hibbing | 9987 | 219
Minnesota | Hutchinson MN | 8330 | 620
Minnesota | International Falls | 10382 | 259
Minnesota | Litchfield | 7734 | 543
Minnesota | Little Falls | 9240 | 385
Minnesota | Mankato | 7716 | 645
Minnesota | Marshall | 7740 | 688
Minnesota | Minneapolis | 7783 | 731
Minnesota | Mora | 8665 | 364
Minnesota | Morris | 8849 | 375
Minnesota | New Ulm | 7646 | 641
Minnesota | Orr | 10534 | 152
Minnesota | Owatonna | 7788 | 641
Minnesota | Park Rapids | 9215 | 236
Minnesota | Pipestone | 8624 | 649
Minnesota | Red Wing | 7935 | 761
Minnesota | Redwood Falls | 7938 | 609
Minnesota | Rochester | 8386 | 488
Minnesota | Roseau | 9817 | 162
Minnesota | Silver Bay | 10453 | 59
Minnesota | St Cloud | 9020 | 444
Minnesota | St Paul | 8019 | 587
Minnesota | Thief River Falls | 9328 | 341
Minnesota | Two Harbors | 9412 | 190
Minnesota | Wheaton | 8713 | 496
Minnesota | Willmar | 7649 | 581
Minnesota | Winona | 7711 | 633
Minnesota | Worthington | 7750 | 644
Mississippi | Biloxi | 1928 | 2606
Mississippi | Columbus MS | 3394 | 2077
Mississippi | Greenville MS | 2432 | 2468
Mississippi | Greenwood | 2552 | 2164
Mississippi | Gulfport | 1619 | 2565
Mississippi | Hattiesburg | 2274 | 2071
Mississippi | Jackson MS | 2428 | 2237
Mississippi | McComb | 2086 | 2315
Mississippi | Meridian | 2417 | 2038
Mississippi | Natchez | 1915 | 2060
Mississippi | Starkville | 3378 | 1962
Mississippi | Tupelo | 3039 | 1905
Missouri | Cape Girardeau | 4506 | 1289
Missouri | Columbia MO | 5307 | 1190
Missouri | Farmington MO | 4527 | 1190
Missouri | Ft. Leonard Wood | 4675 | 1496
Missouri | Jefferson City | 4504 | 1469
Missouri | Joplin | 3663 | 1949
Missouri | Kaiser | 4634 | 1528
Missouri | Kansas City | 5434 | 1316
Missouri | Kirksville | 6397 | 1047
Missouri | Poplar Bluff | 4108 | 1592
Missouri | Springfield MO | 4629 | 1307
Missouri | St. Joseph | 5495 | 1379
Missouri | St. Louis | 4846 | 1555
Missouri | Vichy | 4729 | 924
Missouri | Warrensburg | 4803 | 1344
Montana | Billings | 6731 | 548
Montana | Bozeman | 8354 | 282
Montana | Butte | 9089 | 101
Montana | Cut Bank | 8186 | 86
Montana | Glasgow | 8163 | 504
Montana | Glendive | 8667 | 555
Montana | Great Falls | 7854 | 344
Montana | Havre | 8213 | 432
Montana | Helena | 7587 | 320
Montana | Kalispell | 7928 | 126
Montana | Lewistown | 8014 | 107
Montana | Livingston | 7111 | 370
Montana | Miles City | 7617 | 648
Montana | Missoula | 7323 | 269
Montana | Sidney MT | 9396 | 411
Montana | Wolf Point | 8983 | 249
Nebraska | Ainsworth | 6118 | 789
Nebraska | Alliance | 7026 | 736
Nebraska | Beatrice | 5646 | 1135
Nebraska | Bellevue | 6309 | 1139
Nebraska | Broken Bow | 6772 | 790
Nebraska | Chadron | 6543 | 812
Nebraska | Columbus NC | 6670 | 937
Nebraska | Falls City | 5775 | 1039
Nebraska | Fremont | 6953 | 935
Nebraska | Grand Island | 6654 | 1041
Nebraska | Hastings | 6075 | 1108
Nebraska | Holdrege | 6510 | 852
Nebraska | Imperial NE | 5834 | 1024
Nebraska | Kearney | 6348 | 843
Nebraska | Lincoln | 5892 | 1220
Nebraska | McCook | 5616 | 1256
Nebraska | Norfolk NE | 6943 | 986
Nebraska | North Platte | 6556 | 802
Nebraska | Omaha | 5954 | 1275
Nebraska | O'Neill | 7733 | 847
Nebraska | Ord | 6279 | 872
Nebraska | Scottsbluff | 6560 | 760
Nebraska | Sidney NE | 6864 | 494
Nebraska | Tekamah | 6650 | 1005
Nebraska | Valentine | 6453 | 811
Nevada | Elko | 7070 | 407
Nevada | Ely | 7267 | 154
Nevada | Fallon | 5163 | 1010
Nevada | Las Vegas NV | 2301 | 3187
Nevada | Lovelock | 5351 | 836
Nevada | Mercury | 3001 | 2396
Nevada | Reno | 5488 | 620
Nevada | Tonopah | 5431 | 747
Nevada | Winnemucca | 6158 | 567
New Hampshire | Berlin | 8891 | 145
New Hampshire | Concord NH | 7479 | 397
New Hampshire | Keene | 7169 | 470
New Hampshire | Laconia | 7198 | 396
New Hampshire | Lebanon | 7349 | 389
New Hampshire | Manchester | 6322 | 664
New Hampshire | Mount Washington | 13275 | 0
New Hampshire | Portsmouth | 6753 | 527
New Jersey | Atlantic City | 5073 | 886
New Jersey | Belmar | 5280 | 890
New Jersey | Fairfield NJ | 5060 | 654
New Jersey | Millville | 4680 | 1011
New Jersey | Newark | 5057 | 1237
New Jersey | Rio Grande | 4286 | 1028
New Jersey | Teterboro | 4868 | 695
New Jersey | Trenton | 5040 | 1177
New Mexico | Alamogordo | 3327 | 1793
New Mexico | Albuquerque | 4157 | 1269
New Mexico | Carlsbad NM | 2764 | 2298
New Mexico | Clayton | 4765 | 1156
New Mexico | Clovis | 4467 | 1396
New Mexico | Deming | 2878 | 1891
New Mexico | Farmington NM | 5199 | 1022
New Mexico | Gallup | 6002 | 388
New Mexico | Las Cruces | 2876 | 2146
New Mexico | Las Vegas NM | 5180 | 307
New Mexico | Roswell | 2735 | 1932
New Mexico | Ruidoso | 4095 | 604
New Mexico | Santa Fe | 5449 | 589
New Mexico | Taos | 6904 | 198
New Mexico | Truth or Consequences | 3102 | 1742
New Mexico | Tucumcari | 4109 | 1423
New York | Albany NY | 6773 | 489
New York | Binghamton | 7015 | 404
New York | Buffalo | 6612 | 468
New York | Elmira | 6449 | 297
New York | Glen Falls | 7158 | 481
New York | Jamestown NY | 7188 | 278
New York | Massena | 8046 | 376
New York | Monticello NY | 7059 | 428
New York | New Windsor | 6159 | 756
New York | New York | 4885 | 1133
New York | Nigara Falls | 6484 | 602
New York | Republic | 4893 | 983
New York | Rockester | 6518 | 627
New York | Ronkonkoma | 5005 | 983
New York | Saranac Lake | 9158 | 149
New York | Syracuse | 6609 | 535
New York | Utica | 6974 | 414
New York | Wappingers Falls | 6030 | 607
New York | Watertown NY | 7496 | 330
New York | Westhampton Beach | 5741 | 455
New York | White Plains | 5783 | 595
North Carolina | Asheville | 4273 | 817
North Carolina | Cape Hatteras | 2563 | 1729
North Carolina | Charlotte | 3153 | 1675
North Carolina | Elizabeth City | 2744 | 1760
North Carolina | Fayetteville NC | 3489 | 1576
North Carolina | Goldsboro | 3589 | 1743
North Carolina | Greensboro | 3868 | 1371
North Carolina | Greenville NC | 3040 | 1603
North Carolina | Havelock | 3345 | 1701
North Carolina | Hickory | 3457 | 1416
North Carolina | Jacksonville NC | 3814 | 1370
North Carolina | Kinston | 3397 | 1818
North Carolina | Manteo | 3053 | 1617
North Carolina | New Bern | 2276 | 1874
North Carolina | Raleigh | 3465 | 1566
North Carolina | Rocky Mount | 2878 | 1435
North Carolina | Southern Pines | 3570 | 1496
North Carolina | Wilmington NC | 2401 | 1928
North Carolina | Winston-Salem | 3214 | 1244
North Dakota | Bismarck | 8452 | 453
North Dakota | Devils Lake | 9251 | 288
North Dakota | Dickinson | 9028 | 417
North Dakota | Fargo | 9211 | 491
North Dakota | Grand Forks | 9534 | 486
North Dakota | Jamestown ND | 9505 | 519
North Dakota | Minot | 8972 | 432
North Dakota | Williston | 8467 | 404
Ohio | Akron OH | 259 | 654
Ohio | Cincinnati | 4911 | 1039
Ohio | Cleveland | 6160 | 760
Ohio | Columbus OH | 5599 | 747
Ohio | Dayton | 5945 | 905
Ohio | Findlay | 5590 | 541
Ohio | Mansfield | 6615 | 620
Ohio | Toledo OH | 6515 | 610
Ohio | Youngstown | 6628 | 531
Ohio | Zanesville | 4941 | 702
Oklahoma | Altus | 3164 | 2563
Oklahoma | Bartlesville | 4266 | 1654
Oklahoma | Clinton OK | 4175 | 2023
Oklahoma | Enid | 4466 | 2034
Oklahoma | Fort Sill | 3421 | 2392
Oklahoma | Gage | 4103 | 2013
Oklahoma | Hobart | 3600 | 2377
Oklahoma | Lawton | 3055 | 1979
Oklahoma | McAlester | 3081 | 2086
Oklahoma | Oklahoma City | 3556 | 2038
Oklahoma | Ponca City | 3887 | 2437
Oklahoma | Stillwater | 3799 | 2185
Oklahoma | Tulsa | 3844 | 2066
Oregon | Astoria | 4933 | 48
Oregon | Aurora OR | 4277 | 327
Oregon | Baker City | 7142 | 231
Oregon | Burns | 7201 | 230
Oregon | Corvallus | 4257 | 405
Oregon | Eugene | 4803 | 295
Oregon | Klamath Falls | 6765 | 185
Oregon | La Grande | 6152 | 329
Oregon | Lakeview | 7091 | 199
Oregon | Medford | 4530 | 602
Oregon | North Bend | 4525 | 0
Oregon | Pendleton | 5204 | 585
Oregon | Portland OR | 4187 | 367
Oregon | Redmond | 6583 | 204
Oregon | Roseburg | 3798 | 405
Oregon | Salem | 4583 | 275
Oregon | Sexton Summit | 5657 | 362
Pennsylvania | Allentown | 5651 | 773
Pennsylvania | Altoona | 5917 | 595
Pennsylvania | Bradford | 8204 | 204
Pennsylvania | Butler | 6575 | 481
Pennsylvania | DuBois | 6942 | 386
Pennsylvania | Erie | 6460 | 579
Pennsylvania | Franklin PA | 6830 | 327
Pennsylvania | Harrisburg | 5409 | 927
Pennsylvania | Johnstown | 6516 | 482
Pennsylvania | Lancaster PA | 4955 | 877
Pennsylvania | Middletown | 6105 | 1123
Pennsylvania | Philadelphia | 4824 | 1184
Pennsylvania | Pittsburgh | 5925 | 726
Pennsylvania | Reading | 5067 | 900
Pennsylvania | Scranton | 5216 | 608
Pennsylvania | University Park | 6188 | 585
Pennsylvania | Washington PA | 5727 | 528
Pennsylvania | Williamsport | 5761 | 759
Rhode Island | New Shoreham | 5221 | 435
Rhode Island | Pawtucket | 6466 | 504
Rhode Island | Providence | 5870 | 735
South Carolina | Anderson | 3436 | 1037
South Carolina | Beaufort | 2096 | 2158
South Carolina | Charleston SC | 2051 | 2302
South Carolina | Columbia SC | 2593 | 2020
South Carolina | Florence | 2316 | 2202
South Carolina | Greenville SC | 3652 | 1409
South Carolina | Greer | 3244 | 1553
South Carolina | Myrtle Beach | 2379 | 1870
South Carolina | North Myrtle Beach | 2470 | 1727
South Carolina | Sumter | 3072 | 1706
South Dakota | Aberdeen SD | 7968 | 657
South Dakota | Brookings | 7926 | 449
South Dakota | Huron | 8196 | 638
South Dakota | Mitchell | 7879 | 909
South Dakota | Mobridge | 8474 | 735
South Dakota | Pierre | 7079 | 818
South Dakota | Rapid City | 7203 | 675
South Dakota | Sioux Falls | 7680 | 680
South Dakota | Watertown SD | 8803 | 422
South Dakota | Yankton | 7058 | 996
Tennessee | Blountville | 4439 | 971
Tennessee | Chattanooga | 3224 | 1657
Tennessee | Crossville | 3976 | 933
Tennessee | Dyersburg | 3723 | 1896
Tennessee | Jackson TN | 3339 | 1404
Tennessee | Knoxville TN | 3959 | 1482
Tennessee | Memphis | 2999 | 2134
Tennessee | Nashville | 3737 | 1751
Texas | Abilene | 2968 | 2302
Texas | Alice | 912 | 4033
Texas | Amarillo | 4130 | 1412
Texas | Austin TX | 1269 | 2884
Texas | Brownsville | 750 | 3867
Texas | Childress | 3258 | 2007
Texas | College Station | 1646 | 2670
Texas | Corpus Christi | 934 | 3313
Texas | Cotulla | 918 | 3848
Texas | Dalhart | 5029 | 1041
Texas | Dallas | 2333 | 2678
Texas | Del Rio | 1340 | 3187
Texas | El Paso | 2499 | 2171
Texas | Galveston | 1096 | 3116
Texas | Georgetown | 2070 | 2683
Texas | Greenville TX | 2717 | 2445
Texas | Harlingen | 518 | 3816
Texas | Hondo | 1694 | 2825
Texas | Houston | 1439 | 2974
Texas | Killeen | 2087 | 2721
Texas | Kingsville | 895 | 3419
Texas | Laredo | 1164 | 4080
Texas | Longview | 2131 | 2437
Texas | Lubbock | 3436 | 1699
Texas | Lufkin | 1823 | 2479
Texas | Marfa | 3117 | 1044
Texas | McAllen | 729 | 3903
Texas | McGregor | 2334 | 2614
Texas | Midland | 2482 | 2057
Texas | Mineral wells | 2363 | 2495
Texas | Nacogdockes | 2305 | 2313
Texas | Palacios | 1346 | 3024
Texas | Paris | 3100 | 2057
Texas | Port Arthur | 1422 | 2904
Texas | Rockport | 691 | 3576
Texas | San Angelo | 2485 | 2259
Texas | San Antonio | 1548 | 2992
Texas | Temple | 2260 | 2717
Texas | Tyler | 2339 | 2363
Texas | Victoria | 1309 | 3042
Texas | Waco | 2251 | 2699
Texas | Wichita Falls | 2838 | 2350
Texas | Wink | 2423 | 2932
Utah | Blanding | 5535 | 1171
Utah | Bryce Canyon City | 8955 | 33
Utah | Cedar City | 5776 | 747
Utah | Delta | 6021 | 799
Utah | Hanksville | 5354 | 1445
Utah | Moab | 5106 | 1301
Utah | Ogden | 5831 | 1092
Utah | Provo | 5836 | 858
Utah | Saint George | 2729 | 2936
Utah | Salt Lake City | 5350 | 1118
Utah | Vernal | 6661 | 525
Utah | Wendover | 5970 | 1221
Vermont | Burlington VT | 7491 | 420
Vermont | Montpelier | 7662 | 249
Vermont | Rutland | 7563 | 485
Vermont | Springfield VT | 7264 | 281
Virginia | Abingdon | 4953 | 1011
Virginia | Blacksburg | 5081 | 754
Virginia | Charlottesville | 3697 | 1122
Virginia | Danville | 3707 | 1678
Virginia | Farmville | 4084 | 1323
Virginia | Franklin VA | 3096 | 1557
Virginia | Fredericksburg | 4531 | 1420
Virginia | Hampton | 4195 | 1437
Virginia | Hillsville | 5459 | 604
Virginia | Hot Springs VA | 6585 | 254
Virginia | Leesburg | 5242 | 1189
Virginia | Lynchburg | 4239 | 1305
Virginia | Manassas | 5160 | 935
Virginia | Marion VA | 4817 | 744
Virginia | Martinsville | 4496 | 1133
Virginia | Melfa | 3857 | 1387
Virginia | Newport News | 3436 | 1705
Virginia | Norfolk VA | 3411 | 1630
Virginia | Petersburg VA | 3557 | 1400
Virginia | Pulaski | 3336 | 1539
Virginia | Quantico | 4109 | 1232
Virginia | Richmond | 3883 | 1493
Virginia | Roanoke | 4246 | 1552
Virginia | Virginia Beach | 3336 | 1539
Virginia | Washington DC | 4921 | 1113
Virginia | Weyers Cave | 4878 | 1102
Virginia | Winchester | 5193 | 1196
Virginia | Wise | 4910 | 747
Washington | Aberdeen WA | 5240 | 21
Washington | Bellingham | 5768 | 24
Washington | Bremerton | 5533 | 112
Washington | Ephrata | 5578 | 882
Washington | Everett | 5097 | 69
Washington | Forks | 5682 | 19
Washington | Hanford | 5669 | 1007
Washington | Hoquiam | 5240 | 21
Washington | Kelso | 4682 | 115
Washington | Moses Lake | 5431 | 641
Washington | Olympia | 5331 | 118
Washington | Pasco | 4921 | 711
Washington | Port Angeles | 5945 | 13
Washington | Pullman | 6483 | 234
Washington | Renton | 4378 | 216
Washington | Seattle | 4372 | 169
Washington | Spokane | 6716 | 341
Washington | Stampede Pass | 8898 | 81
Washington | Tacoma | 5664 | 142
Washington | The Dalles | 4501 | 879
Washington | Toledo WA | 5853 | 82
Washington | Walla Walla | 4836 | 839
Washington | Wenatchee | 5748 | 867
Washington | Whidbey Island | 5510 | 0
Washington | Yakima | 6041 | 430
West Virginia | Beckley | 5361 | 631
West Virginia | Bluefield | 4451 | 597
West Virginia | Bridgeport | 5137 | 855
West Virginia | Charleston WV | 4708 | 1015
West Virginia | Elkins | 6050 | 368
West Virginia | Huntington | 4642 | 1077
West Virginia | Lewisburg | 6270 | 432
West Virginia | Martinsburg | 4345 | 761
West Virginia | Morgantown | 5020 | 669
West Virginia | Parkersburg | 4979 | 1101
West Virginia | Wheeling | 5793 | 639
Wisconsin | Antigo | 8664 | 440
Wisconsin | Appleton | 7022 | 517
Wisconsin | Eau Claire | 8475 | 600
Wisconsin | Green Bay | 7853 | 496
Wisconsin | Janesville | 6713 | 295
Wisconsin | La Crosse | 7445 | 748
Wisconsin | Lone Rock | 6651 | 543
Wisconsin | Madison | 7724 | 604
Wisconsin | Manitowac | 7231 | 322
Wisconsin | Marshfield | 7449 | 432
Wisconsin | Milwaukee | 7348 | 545
Wisconsin | Minocqua | 8772 | 410
Wisconsin | Mosinee | 8719 | 401
Wisconsin | Oshkosh | 8013 | 380
Wisconsin | Phillips | 8638 | 337
Wisconsin | Rhinelander | 8823 | 437
Wisconsin | Rice Lake | 8706 | 420
Wisconsin | Sturgeon Bay | 7301 | 424
Wisconsin | Watertown WI | 6864 | 674
Wisconsin | Wausau | 7821 | 658
Wyoming | Casper | 7409 | 440
Wyoming | Cheyenne | 7362 | 265
Wyoming | Cody | 7131 | 436
Wyoming | Evanston | 8339 | 188
Wyoming | Gillette | 6992 | 767
Wyoming | Jackson Hole | 9670 | 15
Wyoming | Lander | 7477 | 432
Wyoming | Laramie | 7799 | 111
Wyoming | Rawlins | 7392 | 289
Wyoming | Riverton | 7579 | 708
Wyoming | Rock Springs | 7971 | 191
Wyoming | Sheridan | 7215 | 399
Wyoming | Worland | 7285 | 611